## Overview
2026-04-16
Terrestrial vs. Orbital Data Centers: A Technical and Financial Analysis
Author: | Michael Pierce
Acronyms
TDC | Terrestrial Data Center
ODC | Orbital Data Center
GPU | Graphical Processing Unit
NPV | Net Present Value
DCF | Discounted Cash Flow
Workbook Tabs
Model | Models, analyses, and main interaction points
TDC Metrics | TDC subsystems' breakdown, sourcing, and rationale of input metrics
Compute Metrics | Shared compute hardware input metrics (breakdown, sourcing, and rationale)
ODC Metrics | ODC subsystems' breakdown, sourcing, and rationale of input metrics
Cell Color Codes:
Section Header
Subsection Header
Input Parameters
Derived or Unchangeable Parameters
Key Output Parameters
Assumptions
TDCs and ODCs will have identical GPU performance attributes.
Assume bit flips from solar radiation do not impact performance of model training noticeably .
The ODC is set in Sun-Synchronous Orbit - maintaining 100% sunlight availability.
Radiators only rejects heat from GPU, not heat of absorption by solar panel.
Both TDCs and ODCs are set to maintain the originally specified compute capability and must replace hardware failures. TDCs only replace GPUs, while ODCs must replace entire satellites.
Launch cost is simply "price per kg to LEO", assuming maximum capacity filled by launch vehicle. Realistic orbital altitudes and inclinations impacting launch density are not considered.
No degradation in performance for space-based solar cells.
System Boundary
Includes | Data center subsystems/components + costs and technologies to deploy the data center and operate/maintain it.
Excludes | NRE, supply chain constraints (LOx, methane, solar panels, GPUs, grid power, etc.), launch vehicle design, ground stations.
© 2026 Technology Strategy Partners ¦ All rights reserved.
Permission is hereby granted to any person obtaining a copy of this software/tool and associated documentation files (the “Software”) to use the Software, provided that this notice is included in all copies or substantial portions of the Software. The software is provided “as is”, without warranty of any kind, express or implied, including but not limited to the warranties of merchantability, fitness for a particular purpose, and non-infringement. In no event shall the authors or copyright holders be liable for any claim, damages, or other liability, whether in an action of contract, tort, or otherwise, arising from, out of, or in connection with the software or the use or other dealings in the software. No support, maintenance, or updates are implied or guaranteed.

## Model
© 2026 Technology Strategy Partners ¦ All rights reserved.
Terrestrial Data Center | [5 empty] | Orbital Data Center | [5 empty] | Orbital Data Center : Launch Cost Break-Even - Tech Today | [7 empty] | Orbital Data Center : Launch Cost Break-Even - Next Gen | [7 empty] | Orbital Data Center : Launch Cost Break-Even - Future Concept
Parameter | Tech Today | Next Gen | Future Concept | Units | Comment | Parameter | Tech Today | Next Gen | Future Concept | Units | Comment | Parameter | Launch Cost | Launch Cost | Launch Cost | Launch Cost | Launch Cost | Units | Comment | Parameter | Launch Cost | Launch Cost | Launch Cost | Launch Cost | Launch Cost | Units | Comment | Parameter | Launch Cost | Launch Cost | Launch Cost | Launch Cost | Launch Cost | Units | Comment
Assumption Level | Conservative | Conservative | Conservative |  |  | Assumption Confidence | Conservative | Moderate | Aggressive |  |  | Assumption Level | 4000 | 3000 | 2000 | 1000 | 0 |  |  | Assumption Level | 4000 | 3000 | 2000 | 1000 | 0 |  |  | Assumption Level | 4000 | 3000 | 2000 | 1000 | 0
Inputs / Model | [5 empty] | Inputs / Model | [5 empty] | Inputs / Model | [7 empty] | Inputs / Model | [7 empty] | Inputs / Model
Key Sizing Metric | [5 empty] | Key Constraint | [5 empty] | Key Constraint | [7 empty] | Key Constraint | [7 empty] | Key Constraint
Compute (IT) Power | 1000 | 1000 | 1000 | MW | Power of useful compute | Compute (IT) Power | 1000 | 1000 | 1000 | MW | To match TDC's useful compute power | Compute (IT) Power | 1000 | 1000 | 1000 | 1000 | 1000 | MW | To match TDC's useful compute power | Compute (IT) Power | 1000 | 1000 | 1000 | 1000 | 1000 | MW | To match TDC's useful compute power | Compute (IT) Power | 1000 | 1000 | 1000 | 1000 | 1000 | MW | To match TDC's useful compute power
Compute (IT) Power (Unit Conversion) | 1000000000 | 1000000000 | 1000000000 | W |  | Compute (IT) Power (Unit Conversion) | 1000000000 | 1000000000 | 1000000000 | W |  | Compute (IT) Power (Unit Conversion) | 1000000000 | 1000000000 | 1000000000 | 1000000000 | 1000000000 | W |  | Compute (IT) Power (Unit Conversion) | 1000000000 | 1000000000 | 1000000000 | 1000000000 | 1000000000 | W |  | Compute (IT) Power (Unit Conversion) | 1000000000 | 1000000000 | 1000000000 | 1000000000 | 1000000000 | W
Power Subsystem | [5 empty] | Power Subsystem | [5 empty] | Power Subsystem | [7 empty] | Power Subsystem | [7 empty] | Power Subsystem
Power Usage Effectiveness (PUE) | 1.3 | 1.1 | 1.05 |  | Total Factility Power / IT (Compute) Power | Specific Cost | 50 | 29.62 | 15 | $/W |  | Specific Cost | 50 | 50 | 50 | 50 | 50 | $/W |  | Specific Cost | 29.62 | 29.62 | 29.62 | 29.62 | 29.62 | $/W |  | Specific Cost | 15 | 15 | 15 | 15 | 15 | $/W
Electricity Price | 0.06 | 0.08 | 0.1 | $/kWh |  | Specific Mass | 0.010417 | 0.0033003 | 0.00033333 | kg/W |  | Specific Mass | 0.010417 | 0.010417 | 0.010417 | 0.010417 | 0.010417 | kg/W |  | Specific Mass | 0.0033003 | 0.0033003 | 0.0033003 | 0.0033003 | 0.0033003 | kg/W |  | Specific Mass | 0.00033333 | 0.00033333 | 0.00033333 | 0.00033333 | 0.00033333 | kg/W
Facility Power | 1300000000 | 1100000000 | 1050000000 | W | IT Power * PUE | Power Subsystem CapEx | 50000000000 | 29620000000 | 15000000000 | $ |  | Power Subsystem CapEx | 50000000000 | 50000000000 | 50000000000 | 50000000000 | 50000000000 | $ |  | Power Subsystem CapEx | 29620000000 | 29620000000 | 29620000000 | 29620000000 | 29620000000 | $ |  | Power Subsystem CapEx | 15000000000 | 15000000000 | 15000000000 | 15000000000 | 15000000000 | $
Average Facility Power | 1040000000 | 880000000 | 840000000 | W | Taking into account average power of GPU load | Total Mass | 10416666.6667 | 3300330.033 | 333333.3333 | kg |  | Total Mass | 10416666.6667 | 10416666.6667 | 10416666.6667 | 10416666.6667 | 10416666.6667 | kg |  | Total Mass | 3300330.033 | 3300330.033 | 3300330.033 | 3300330.033 | 3300330.033 | kg |  | Total Mass | 333333.3333 | 333333.3333 | 333333.3333 | 333333.3333 | 333333.3333 | kg
Annual Facility Energy Consumption | 9110400000000 | 7708800000000 | 7358400000000 | Wh
Annual Energy Cost | 546624000 | 616704000 | 735840000 | $/year
Power Subsystem OpEx | 546624000 | 616704000 | 735840000 | $/year
Compute Subsystem | [5 empty] | Compute Subsystem | [5 empty] | Compute Subsystem | [7 empty] | Compute Subsystem | [7 empty] | Compute Subsystem
GPU Selection | H100 SXM | Estimated (5-year) | Estimated (10-year) |  |  | GPU Name | H100 SXM | Estimated (5-year) | Estimated (10-year) |  |  | GPU Name | H100 SXM | H100 SXM | H100 SXM | H100 SXM | H100 SXM |  |  | GPU Name | Estimated (5-year) | Estimated (5-year) | Estimated (5-year) | Estimated (5-year) | Estimated (5-year) |  |  | GPU Name | Estimated (10-year) | Estimated (10-year) | Estimated (10-year) | Estimated (10-year) | Estimated (10-year)
GPU Unit Cost | 30000 | 52000 | 90000 | $/GPU |  | GPU Unit Cost | 30000 | 52000 | 90000 | $/GPU |  | GPU Unit Cost | 30000 | 30000 | 30000 | 30000 | 30000 | $/GPU |  | GPU Unit Cost | 52000 | 52000 | 52000 | 52000 | 52000 | $/GPU |  | GPU Unit Cost | 90000 | 90000 | 90000 | 90000 | 90000 | $/GPU
GPU TDP | 700 | 1050 | 1580 | W/GPU |  | GPU TDP | 700 | 1050 | 1580 | W/GPU |  | GPU TDP | 700 | 700 | 700 | 700 | 700 | W/GPU |  | GPU TDP | 1050 | 1050 | 1050 | 1050 | 1050 | W/GPU |  | GPU TDP | 1580 | 1580 | 1580 | 1580 | 1580 | W/GPU
GPU Average Power Percentage | 80% | 0.8 | 0.8 |  |  | GPU Average Power Percentage | 80% | 80% | 80% |  |  | GPU Average Power Percentage | 80% | 80% | 80% | 80% | 80% |  |  | GPU Average Power Percentage | 80% | 80% | 80% | 80% | 80% |  |  | GPU Average Power Percentage | 80% | 80% | 80% | 80% | 80%
Effective Rated Design Power | 1275 | 1910 | 2870 | W/GPU |  | Effective Rated Design Power | 1275 | 1910 | 2870 | W/GPU |  | Effective Rated Design Power | 1275 | 1275 | 1275 | 1275 | 1275 | W/GPU |  | Effective Rated Design Power | 1910 | 1910 | 1910 | 1910 | 1910 | W/GPU |  | Effective Rated Design Power | 2870 | 2870 | 2870 | 2870 | 2870 | W/GPU
Base GPU Performance | 1979 | 8400 | 35600 | TFLOPS/GPU |  | GPU Performance | 1979 | 8400 | 35600 | TFLOPS/GPU |  | GPU Performance | 1979 | 1979 | 1979 | 1979 | 1979 | TFLOPS/GPU |  | GPU Performance | 8400 | 8400 | 8400 | 8400 | 8400 | TFLOPS/GPU |  | GPU Performance | 35600 | 35600 | 35600 | 35600 | 35600 | TFLOPS/GPU
Compute Failure Rate | 0.8% | 0.8% | 0.8% | %/year |  | Compute Failure Rate | 0.8% | 0.8% | 0.8% | %/year |  | Compute Failure Rate | 0.8% | 0.8% | 0.8% | 0.8% | 0.8% | %/year |  | Compute Failure Rate | 0.8% | 0.8% | 0.8% | 0.8% | 0.8% | %/year |  | Compute Failure Rate | 0.8% | 0.8% | 0.8% | 0.8% | 0.8% | %/year
Non-GPU Hardware CapEx Scale | 52% | 52% | 52% | %/GPU_$ | CPUs, networking devices, storage, etc. | GPU Mass | 1.5 | 2 | 2.8 | kg |  | GPU Mass | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | kg |  | GPU Mass | 2 | 2 | 2 | 2 | 2 | kg |  | GPU Mass | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | kg
Network & Software OpEx Scale | 0.36 | 0.36 | 0.36 | $/W | Connectivity, licensing, cybersecutiy, compliance | New GPU Model Rate | 2 | 2 | 2 | years | Same as TDC | New GPU Model Rate | 2 | 2 | 2 | 2 | 2 | years | Same as TDC | New GPU Model Rate | 2 | 2 | 2 | 2 | 2 | years | Same as TDC | New GPU Model Rate | 2 | 2 | 2 | 2 | 2 | years | Same as TDC
New GPU Model Rate | 2 | 2 | 2 | years |  | GPU Performance Improvement Per Refresh | 50% | 50% | 50% |  | Assuming price remains constant | GPU Performance Improvement Per Refresh | 50% | 50% | 50% | 50% | 50% |  | Assuming price remains constant | GPU Performance Improvement Per Refresh | 50% | 50% | 50% | 50% | 50% |  | Assuming price remains constant | GPU Performance Improvement Per Refresh | 50% | 50% | 50% | 50% | 50% |  | Assuming price remains constant
GPU Performance Improvement Per Refresh | 50% | 50% | 50% |  | Assuming price remains constant | Specific Cost | 23.5294 | 27.2251 | 31.3589 | $/W |  | Specific Cost | 23.5294 | 23.5294 | 23.5294 | 23.5294 | 23.5294 | $/W |  | Specific Cost | 27.2251 | 27.2251 | 27.2251 | 27.2251 | 27.2251 | $/W |  | Specific Cost | 31.3589 | 31.3589 | 31.3589 | 31.3589 | 31.3589 | $/W
GPU Average Power | 560 | 840 | 1264 | W/GPU |  | Specific Mass | 0.0011765 | 0.0010471 | 0.00097561 | kg/W |  | Specific Mass | 0.0011765 | 0.0011765 | 0.0011765 | 0.0011765 | 0.0011765 | kg/W |  | Specific Mass | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | 0.0010471 | kg/W |  | Specific Mass | 0.00097561 | 0.00097561 | 0.00097561 | 0.00097561 | 0.00097561 | kg/W
Number of GPUs | 784313.7255 | 523560.2094 | 348432.0557 | GPUs |  | Number of GPUs in Operation | 784313.7255 | 523560.2094 | 348432.0557 | GPUs |  | Number of GPUs in Operation | 784313.7255 | 784313.7255 | 784313.7255 | 784313.7255 | 784313.7255 | GPUs |  | Number of GPUs in Operation | 523560.2094 | 523560.2094 | 523560.2094 | 523560.2094 | 523560.2094 | GPUs |  | Number of GPUs in Operation | 348432.0557 | 348432.0557 | 348432.0557 | 348432.0557 | 348432.0557 | GPUs
GPU CapEx | 23529411764.7059 | 27225130890.0524 | 31358885017.4216 | $ |  | Number of Spare GPUs | 31372.549 | 20942.4084 | 13937.2822 | GPUs |  | Number of Spare GPUs | 31372.549 | 31372.549 | 31372.549 | 31372.549 | 31372.549 | GPUs |  | Number of Spare GPUs | 20942.4084 | 20942.4084 | 20942.4084 | 20942.4084 | 20942.4084 | GPUs |  | Number of Spare GPUs | 13937.2822 | 13937.2822 | 13937.2822 | 13937.2822 | 13937.2822 | GPUs
Non-GPU Hardware CapEx | 12235294117.6471 | 14157068062.8272 | 16306620209.0592 | $ |  | Compute CapEx | 24470588235.2941 | 28314136125.6545 | 32613240418.1185 | $ |  | Compute CapEx | 24470588235.2941 | 24470588235.2941 | 24470588235.2941 | 24470588235.2941 | 24470588235.2941 | $ |  | Compute CapEx | 28314136125.6545 | 28314136125.6545 | 28314136125.6545 | 28314136125.6545 | 28314136125.6545 | $ |  | Compute CapEx | 32613240418.1185 | 32613240418.1185 | 32613240418.1185 | 32613240418.1185 | 32613240418.1185 | $
Compute Subsystem CapEx | 35764705882.3529 | 41382198952.8796 | 47665505226.4808 | $ |  | Total Mass | 1223529.4118 | 1089005.2356 | 1014634.1463 | kg |  | Total Mass | 1223529.4118 | 1223529.4118 | 1223529.4118 | 1223529.4118 | 1223529.4118 | kg |  | Total Mass | 1089005.2356 | 1089005.2356 | 1089005.2356 | 1089005.2356 | 1089005.2356 | kg |  | Total Mass | 1014634.1463 | 1014634.1463 | 1014634.1463 | 1014634.1463 | 1014634.1463 | kg
Annual Spares/Replacement | 6275 | 4188 | 2787 | GPUs/year
Annual Replacement Cost | 188250000 | 217776000 | 250830000 | $/year | Assuming negligible labor cost
Network & Software OpEx | 360000000 | 360000000 | 360000000 | $/year
Compute Subsystem OpEx | 548250000 | 577776000 | 610830000 | $/year
Cooling Subsystem | [5 empty] | Cooling Subsystem | [5 empty] | Cooling Subsystem | [7 empty] | Cooling Subsystem | [7 empty] | Cooling Subsystem
Water Usage Effectiveness (WUE) | 1.8 | 0.2 | 0 | L/kWh |  | Operating Temperature | 350 | 400 | 500 | K |  | Operating Temperature | 350 | 350 | 350 | 350 | 350 | K |  | Operating Temperature | 400 | 400 | 400 | 400 | 400 | K |  | Operating Temperature | 500 | 500 | 500 | 500 | 500 | K
Water Price | 0.00613 | 0.00711 | 0.00824 | $/gal |  | Emissivity (epsilon) | 0.91 | 0.95 | 0.97 |  |  | Emissivity (epsilon) | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 |  |  | Emissivity (epsilon) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 |  |  | Emissivity (epsilon) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
Yearly Water Usage | 4165918097.7543 | 462879788.6394 | 0 | gal/year | 3.785 liters / gallon | Mass / Area | 6 | 5 | 4 | kg/m^2 |  | Mass / Area | 6 | 6 | 6 | 6 | 6 | kg/m^2 |  | Mass / Area | 5 | 5 | 5 | 5 | 5 | kg/m^2 |  | Mass / Area | 4 | 4 | 4 | 4 | 4 | kg/m^2
Yearly Water Cost | 25537077.9392 | 3291075.2972 | 0 | $/year |  | Cost / Area | 210 | 189 | 170 | $/m^2 |  | Cost / Area | 210 | 210 | 210 | 210 | 210 | $/m^2 |  | Cost / Area | 189 | 189 | 189 | 189 | 189 | $/m^2 |  | Cost / Area | 170 | 170 | 170 | 170 | 170 | $/m^2
Cooling Subsystem OpEx | 25537077.9392 | 3291075.2972 | 0 | $/year |  | Space Temperature | 3 | 3 | 3 | K | Constant | Space Temperature | 3 | 3 | 3 | 3 | 3 | K | Constant | Space Temperature | 3 | 3 | 3 | 3 | 3 | K | Constant | Space Temperature | 3 | 3 | 3 | 3 | 3 | K | Constant
[6 empty] | Stefan-Boltzmann constant (sigma) | 5.67e-08 | 5.67e-08 | 5.67e-08 | W/(m^2*K^4) | Constant | Stefan-Boltzmann constant (sigma) | 5.67e-08 | 5.67e-08 | 5.67e-08 | 5.67e-08 | 5.67e-08 | W/(m^2*K^4) | Constant | Stefan-Boltzmann constant (sigma) | 5.67e-08 | 5.67e-08 | 5.67e-08 | 5.67e-08 | 5.67e-08 | W/(m^2*K^4) | Constant | Stefan-Boltzmann constant (sigma) | 5.67e-08 | 5.67e-08 | 5.67e-08 | 5.67e-08 | 5.67e-08 | W/(m^2*K^4) | Constant
[6 empty] | Heat Rejection / Area | 774.2775 | 1378.944 | 3437.4375 | W/m^2 |  | Heat Rejection / Area | 774.2775 | 774.2775 | 774.2775 | 774.2775 | 774.2775 | W/m^2 |  | Heat Rejection / Area | 1378.944 | 1378.944 | 1378.944 | 1378.944 | 1378.944 | W/m^2 |  | Heat Rejection / Area | 3437.4375 | 3437.4375 | 3437.4375 | 3437.4375 | 3437.4375 | W/m^2
[6 empty] | Specific Cost | 0.27122 | 0.13706 | 0.049455 | $/W |  | Specific Cost | 0.27122 | 0.27122 | 0.27122 | 0.27122 | 0.27122 | $/W |  | Specific Cost | 0.13706 | 0.13706 | 0.13706 | 0.13706 | 0.13706 | $/W |  | Specific Cost | 0.049455 | 0.049455 | 0.049455 | 0.049455 | 0.049455 | $/W
[6 empty] | Specific Mass | 0.0077492 | 0.003626 | 0.0011637 | kg/W |  | Specific Mass | 0.0077492 | 0.0077492 | 0.0077492 | 0.0077492 | 0.0077492 | kg/W |  | Specific Mass | 0.003626 | 0.003626 | 0.003626 | 0.003626 | 0.003626 | kg/W |  | Specific Mass | 0.0011637 | 0.0011637 | 0.0011637 | 0.0011637 | 0.0011637 | kg/W
[6 empty] | Cooling Subsystem CapEx | 271220597.5492 | 137061403.9424 | 49455444.7085 | $ |  | Cooling Subsystem CapEx | 271220597.5492 | 271220597.5492 | 271220597.5492 | 271220597.5492 | 271220597.5492 | $ |  | Cooling Subsystem CapEx | 137061403.9424 | 137061403.9424 | 137061403.9424 | 137061403.9424 | 137061403.9424 | $ |  | Cooling Subsystem CapEx | 49455444.7085 | 49455444.7085 | 49455444.7085 | 49455444.7085 | 49455444.7085 | $
[6 empty] | Total Mass | 7749159.93 | 3625963.0673 | 1163657.5226 | kg |  | Total Mass | 7749159.93 | 7749159.93 | 7749159.93 | 7749159.93 | 7749159.93 | kg |  | Total Mass | 3625963.0673 | 3625963.0673 | 3625963.0673 | 3625963.0673 | 3625963.0673 | kg |  | Total Mass | 1163657.5226 | 1163657.5226 | 1163657.5226 | 1163657.5226 | 1163657.5226 | kg
Deployment (Integration & Operations) | [5 empty] | Deployment (Integration & Operations) | [5 empty] | Deployment (Integration & Operations) | [7 empty] | Deployment (Integration & Operations) | [7 empty] | Deployment (Integration & Operations)
Powered Shell Scale | 12 | 14.6 | 17.8 | $/W | Land, building, mechanical, electrical | Integration Systems Mass Factor | 40.9% | 40.9% | 40.9% |  | % of satellite bus (less payload) | Integration Systems Mass Factor | 40.9% | 40.9% | 40.9% | 40.9% | 40.9% |  | % of satellite bus (less payload) | Integration Systems Mass Factor | 40.9% | 40.9% | 40.9% | 40.9% | 40.9% |  | % of satellite bus (less payload) | Integration Systems Mass Factor | 40.9% | 40.9% | 40.9% | 40.9% | 40.9% |  | % of satellite bus (less payload)
Maintenance & Staffing OpEx Scale | 0.36 | 0.36 | 0.36 | $/W/year | Maintenance for power/cooling/building + staff | Integration Systems Cost Factor | 30% | 25% | 20% |  | % of satellite bus (less payload) | Integration Systems Cost Factor | 30% | 30% | 30% | 30% | 30% |  | % of satellite bus (less payload) | Integration Systems Cost Factor | 25% | 25% | 25% | 25% | 25% |  | % of satellite bus (less payload) | Integration Systems Cost Factor | 20% | 20% | 20% | 20% | 20% |  | % of satellite bus (less payload)
Property Taxes | 0.17 | 0.21697 | 0.27691 | $/W/year | Total tax burden per year | Power/Compute/Cooling Mass | 19389356.0084 | 8015298.3359 | 2511625.0022 | kg |  | Power/Compute/Cooling Mass | 19389356.0084 | 19389356.0084 | 19389356.0084 | 19389356.0084 | 19389356.0084 | kg |  | Power/Compute/Cooling Mass | 8015298.3359 | 8015298.3359 | 8015298.3359 | 8015298.3359 | 8015298.3359 | kg |  | Power/Compute/Cooling Mass | 2511625.0022 | 2511625.0022 | 2511625.0022 | 2511625.0022 | 2511625.0022 | kg
Permitting, Construction, & Commissioning | 3 | 2 | 1.5 | years |  | Integration Systems Mass | 13418352.9737 | 5546966.1918 | 1738163.4956 | kg |  | Integration Systems Mass | 13418352.9737 | 13418352.9737 | 13418352.9737 | 13418352.9737 | 13418352.9737 | kg |  | Integration Systems Mass | 5546966.1918 | 5546966.1918 | 5546966.1918 | 5546966.1918 | 5546966.1918 | kg |  | Integration Systems Mass | 1738163.4956 | 1738163.4956 | 1738163.4956 | 1738163.4956 | 1738163.4956 | kg
Facility Lifetime | 20 | 20 | 20 | years |  | Total System Mass | 32807708.9821 | 13562264.5277 | 4249788.4978 | kg |  | Total System Mass | 32807708.9821 | 32807708.9821 | 32807708.9821 | 32807708.9821 | 32807708.9821 | kg |  | Total System Mass | 13562264.5277 | 13562264.5277 | 13562264.5277 | 13562264.5277 | 13562264.5277 | kg |  | Total System Mass | 4249788.4978 | 4249788.4978 | 4249788.4978 | 4249788.4978 | 4249788.4978 | kg
Data Center GPU Refresh Rate | 5 | 5 | 5 | years |  | Power Subsystem Cost | 50000000000 | 29620000000 | 15000000000 | $ |  | Power Subsystem Cost | 50000000000 | 50000000000 | 50000000000 | 50000000000 | 50000000000 | $ |  | Power Subsystem Cost | 29620000000 | 29620000000 | 29620000000 | 29620000000 | 29620000000 | $ |  | Power Subsystem Cost | 15000000000 | 15000000000 | 15000000000 | 15000000000 | 15000000000 | $
Powered Shell CapEx | 12000000000 | 14600000000 | 17800000000 | $ |  | Compute Cost | 24470588235.2941 | 28314136125.6545 | 32613240418.1185 | $ |  | Compute Cost | 24470588235.2941 | 24470588235.2941 | 24470588235.2941 | 24470588235.2941 | 24470588235.2941 | $ |  | Compute Cost | 28314136125.6545 | 28314136125.6545 | 28314136125.6545 | 28314136125.6545 | 28314136125.6545 | $ |  | Compute Cost | 32613240418.1185 | 32613240418.1185 | 32613240418.1185 | 32613240418.1185 | 32613240418.1185 | $
Maintenance & Staffing OpEx | 360000000 | 360000000 | 360000000 | $/year |  | Radiator Cost | 271220597.5492 | 137061403.9424 | 49455444.7085 | $ |  | Radiator Cost | 271220597.5492 | 271220597.5492 | 271220597.5492 | 271220597.5492 | 271220597.5492 | $ |  | Radiator Cost | 137061403.9424 | 137061403.9424 | 137061403.9424 | 137061403.9424 | 137061403.9424 | $ |  | Radiator Cost | 49455444.7085 | 49455444.7085 | 49455444.7085 | 49455444.7085 | 49455444.7085 | $
Property Tax OpEx | 170000000 | 216967865.625 | 276912086.5522 | $/year |  | Integration Systems Cost | 32032203785.5043 | 19357065843.199 | 11915673965.7068 | $ |  | Integration Systems Cost | 32032203785.5043 | 32032203785.5043 | 32032203785.5043 | 32032203785.5043 | 32032203785.5043 | $ |  | Integration Systems Cost | 19357065843.199 | 19357065843.199 | 19357065843.199 | 19357065843.199 | 19357065843.199 | $ |  | Integration Systems Cost | 11915673965.7068 | 11915673965.7068 | 11915673965.7068 | 11915673965.7068 | 11915673965.7068 | $
Cost of GPU Refresh | 23529411764.7059 | 27225130890.0524 | 31358885017.4216 | $ | Compute CapEx | Total Satellite Material Cost | 106774012618.3476 | 77428263372.7959 | 59578369828.5338 | $ |  | Total Satellite Material Cost | 106774012618.3476 | 106774012618.3476 | 106774012618.3476 | 106774012618.3476 | 106774012618.3476 | $ |  | Total Satellite Material Cost | 77428263372.7959 | 77428263372.7959 | 77428263372.7959 | 77428263372.7959 | 77428263372.7959 | $ |  | Total Satellite Material Cost | 59578369828.5338 | 59578369828.5338 | 59578369828.5338 | 59578369828.5338 | 59578369828.5338 | $
Amortized GPU Refresh OpEx | 4705882352.9412 | 5445026178.0105 | 6271777003.4843 | $/year |  | Launch Vehicle Payload to Orbit | 17500 | 100000 | 200000 | kg/launch |  | Launch Vehicle Payload to Orbit | 17500 | 17500 | 17500 | 17500 | 17500 | kg/launch |  | Launch Vehicle Payload to Orbit | 100000 | 100000 | 100000 | 100000 | 100000 | kg/launch |  | Launch Vehicle Payload to Orbit | 200000 | 200000 | 200000 | 200000 | 200000 | kg/launch
Deployment Environment OpEx | 5235882352.9412 | 6021994043.6355 | 6908689090.0365 | $/year |  | Launch Vehicle Price per Launch | 70000000 | 90000000 | 20000000 | $ | Assumes LEO | Launch Vehicle Price per Launch | 70000000 | 52500000 | 35000000 | 17500000 | 0 | $ | Assumes LEO | Launch Vehicle Price per Launch | 400000000 | 300000000 | 200000000 | 100000000 | 0 | $ | Assumes LEO | Launch Vehicle Price per Launch | 800000000 | 600000000 | 400000000 | 200000000 | 0 | $ | Assumes LEO
Time to Operation | 3 | 2 | 1.5 | years |  | Annual Launch Rate | 167 | 52 | 365 | launches/year |  | Annual Launch Rate | 167 | 167 | 167 | 167 | 167 | launches/year |  | Annual Launch Rate | 52 | 52 | 52 | 52 | 52 | launches/year |  | Annual Launch Rate | 365 | 365 | 365 | 365 | 365 | launches/year
[6 empty] | Constellation Operations Cost | 250000000 | 250000000 | 250000000 | $/year | Annual steady-state ground ops, flight dynamics, and software for the constellation | Constellation Operations Cost | 250000000 | 250000000 | 250000000 | 250000000 | 250000000 | $/year | Annual steady-state ground ops, flight dynamics, and software for the constellation | Constellation Operations Cost | 250000000 | 250000000 | 250000000 | 250000000 | 250000000 | $/year | Annual steady-state ground ops, flight dynamics, and software for the constellation | Constellation Operations Cost | 250000000 | 250000000 | 250000000 | 250000000 | 250000000 | $/year | Annual steady-state ground ops, flight dynamics, and software for the constellation
[6 empty] | Satellite Lifetime | 5 | 5 | 5 | years |  | Satellite Lifetime | 5 | 5 | 5 | 5 | 5 | years |  | Satellite Lifetime | 5 | 5 | 5 | 5 | 5 | years |  | Satellite Lifetime | 5 | 5 | 5 | 5 | 5 | years
[6 empty] | Number of launches | 1874.7262 | 135.6226 | 21.2489 | launches |  | Number of launches | 1874.7262 | 1874.7262 | 1874.7262 | 1874.7262 | 1874.7262 | launches |  | Number of launches | 135.6226 | 135.6226 | 135.6226 | 135.6226 | 135.6226 | launches |  | Number of launches | 21.2489 | 21.2489 | 21.2489 | 21.2489 | 21.2489 | launches
[6 empty] | Launch cost | 131230835928.3181 | 12206038074.9225 | 424978849.7849 | $ | Assumes 100% mass and volume utilization | Launch cost | 131230835928.3181 | 98423126946.2386 | 65615417964.1591 | 32807708982.0795 | 0 | $ | Assumes 100% mass and volume utilization | Launch cost | 54249058110.7667 | 40686793583.0751 | 27124529055.3834 | 13562264527.6917 | 0 | $ | Assumes 100% mass and volume utilization | Launch cost | 16999153991.3958 | 12749365493.5469 | 8499576995.6979 | 4249788497.849 | 0 | $ | Assumes 100% mass and volume utilization
[6 empty] | Deployment Environment CapEx | 163263039713.8224 | 31563103918.1215 | 12340652815.4916 | $ |  | Deployment Environment CapEx | 163263039713.8224 | 130455330731.7429 | 97647621749.6633 | 64839912767.5838 | 32032203785.5043 | $ |  | Deployment Environment CapEx | 73606123953.9657 | 60043859426.274 | 46481594898.5823 | 32919330370.8906 | 19357065843.199 | $ |  | Deployment Environment CapEx | 28914827957.1026 | 24665039459.2536 | 20415250961.4047 | 16165462463.5557 | 11915673965.7068 | $
[6 empty] | Cost of GPU Refresh | 163263039713.8224 | 31563103918.1215 | 12340652815.4916 | $ | Total CapEx (satellites + launch) | Cost of GPU Refresh | 163263039713.8224 | 130455330731.7429 | 97647621749.6633 | 64839912767.5838 | 32032203785.5043 | $ | Total CapEx (satellites + launch) | Cost of GPU Refresh | 73606123953.9657 | 60043859426.274 | 46481594898.5823 | 32919330370.8906 | 19357065843.199 | $ | Total CapEx (satellites + launch) | Cost of GPU Refresh | 28914827957.1026 | 24665039459.2536 | 20415250961.4047 | 16165462463.5557 | 11915673965.7068 | $ | Total CapEx (satellites + launch)
[6 empty] | Amortized GPU Refresh OpEx | 32652607942.7645 | 6312620783.6243 | 2468130563.0983 | $/year |  | Amortized GPU Refresh OpEx | 32652607942.7645 | 26091066146.3486 | 19529524349.9327 | 12967982553.5168 | 6406440757.1009 | $/year |  | Amortized GPU Refresh OpEx | 14721224790.7931 | 12008771885.2548 | 9296318979.7165 | 6583866074.1781 | 3871413168.6398 | $/year |  | Amortized GPU Refresh OpEx | 5782965591.4205 | 4933007891.8507 | 4083050192.2809 | 3233092492.7111 | 2383134793.1414 | $/year
[6 empty] | Deployment Environment OpEx | 32902607942.7645 | 6562620783.6243 | 2718130563.0983 | $/year |  | Deployment Environment OpEx | 32902607942.7645 | 26341066146.3486 | 19779524349.9327 | 13217982553.5168 | 6656440757.1009 | $/year |  | Deployment Environment OpEx | 14971224790.7931 | 12258771885.2548 | 9546318979.7165 | 6833866074.1781 | 4121413168.6398 | $/year |  | Deployment Environment OpEx | 6032965591.4205 | 5183007891.8507 | 4333050192.2809 | 3483092492.7111 | 2633134793.1414 | $/year
[6 empty] | Time to Operation | 11.2259 | 2.6081 | 0.058216 | years | Assumes satellites are ready to go | Time to Operation | 11.2259 | 11.2259 | 11.2259 | 11.2259 | 11.2259 | years | Assumes satellites are ready to go | Time to Operation | 2.6081 | 2.6081 | 2.6081 | 2.6081 | 2.6081 | years | Assumes satellites are ready to go | Time to Operation | 0.058216 | 0.058216 | 0.058216 | 0.058216 | 0.058216 | years | Assumes satellites are ready to go
Outputs | [5 empty] | Outputs | [5 empty] | Outputs | [7 empty] | Outputs | [7 empty] | Outputs
Financials | [5 empty] | Price | [5 empty] | Price | [7 empty] | Price | [7 empty] | Price
Power CapEx |  |  |  |  | CapEx costs are under Deployment's "Powered Shell" | Power CapEx | 50 | 29.62 | 15 | $B |  | Power CapEx | 50 | 50 | 50 | 50 | 50 | $B |  | Power CapEx | 29.62 | 29.62 | 29.62 | 29.62 | 29.62 | $B |  | Power CapEx | 15 | 15 | 15 | 15 | 15 | $B
Compute CapEx | 35.7647 | 41.3822 | 47.6655 | $B | GPUs + non-GPU IT Hardware | Compute CapEx | 24.4706 | 28.3141 | 32.6132 | $B |  | Compute CapEx | 24.4706 | 24.4706 | 24.4706 | 24.4706 | 24.4706 | $B |  | Compute CapEx | 28.3141 | 28.3141 | 28.3141 | 28.3141 | 28.3141 | $B |  | Compute CapEx | 32.6132 | 32.6132 | 32.6132 | 32.6132 | 32.6132 | $B
Cooling CapEx |  |  |  |  | CapEx costs are under Deployment's "Powered Shell" | Cooling CapEx | 0.27122 | 0.13706 | 0.049455 | $B |  | Cooling CapEx | 0.27122 | 0.27122 | 0.27122 | 0.27122 | 0.27122 | $B |  | Cooling CapEx | 0.13706 | 0.13706 | 0.13706 | 0.13706 | 0.13706 | $B |  | Cooling CapEx | 0.049455 | 0.049455 | 0.049455 | 0.049455 | 0.049455 | $B
Deployment CapEx | 12 | 14.6 | 17.8 | $B | Land, building, mechanical, electrical | Deployment CapEx | 163.263 | 31.5631 | 12.3407 | $B |  | Deployment CapEx | 163.263 | 130.4553 | 97.6476 | 64.8399 | 32.0322 | $B |  | Deployment CapEx | 73.6061 | 60.0439 | 46.4816 | 32.9193 | 19.3571 | $B |  | Deployment CapEx | 28.9148 | 24.665 | 20.4153 | 16.1655 | 11.9157 | $B
Total CapEx | 47.7647 | 55.9822 | 65.4655 | $B |  | Total CapEx | 238.0048 | 89.6343 | 60.0033 | $B |  | Total CapEx | 238.0048 | 205.1971 | 172.3894 | 139.5817 | 106.774 | $B |  | Total CapEx | 131.6773 | 118.1151 | 104.5528 | 90.9905 | 77.4283 | $B |  | Total CapEx | 76.5775 | 72.3277 | 68.0779 | 63.8282 | 59.5784 | $B
Total CapEx | 47764705882.3529 | 55982198952.8796 | 65465505226.4808 | $ |  | Total CapEx | 238004848546.6657 | 89634301447.7184 | 60003348678.3187 | $
Power OpEx | 546.624 | 616.704 | 735.84 | $M/year | Power cost | Power OpEx | 0 | 0 | 0 | $M/year |  | Power OpEx | 0 | 0 | 0 | 0 | 0 | $M/year |  | Power OpEx | 0 | 0 | 0 | 0 | 0 | $M/year |  | Power OpEx | 0 | 0 | 0 | 0 | 0 | $M/year
Compute OpEx | 548.25 | 577.776 | 610.83 | $M/year | Failure rate, network, and licensing costs | Compute OpEx | 0 | 0 | 0 | $M/year |  | Compute OpEx | 0 | 0 | 0 | 0 | 0 | $M/year |  | Compute OpEx | 0 | 0 | 0 | 0 | 0 | $M/year |  | Compute OpEx | 0 | 0 | 0 | 0 | 0 | $M/year
Cooling OpEx | 25.5371 | 3.2911 | 0 | $M/year | Water cost | Cooling OpEx | 0 | 0 | 0 | $M/year |  | Cooling OpEx | 0 | 0 | 0 | 0 | 0 | $M/year |  | Cooling OpEx | 0 | 0 | 0 | 0 | 0 | $M/year |  | Cooling OpEx | 0 | 0 | 0 | 0 | 0 | $M/year
Deployment OpEx | 5235.8824 | 6021.994 | 6908.6891 | $M/year | Maintenance of everything, human costs | Deployment OpEx | 32902.6079 | 6562.6208 | 2718.1306 | $M/year | Support staff, controls, amortized fleet refresh | Deployment OpEx | 32902.6079 | 26341.0661 | 19779.5243 | 13217.9826 | 6656.4408 | $M/year | Support staff, controls, amortized fleet refresh | Deployment OpEx | 14971.2248 | 12258.7719 | 9546.319 | 6833.8661 | 4121.4132 | $M/year | Support staff, controls, amortized fleet refresh | Deployment OpEx | 6032.9656 | 5183.0079 | 4333.0502 | 3483.0925 | 2633.1348 | $M/year | Support staff, controls, amortized fleet refresh
Total Annual OpEx | 6356.2934 | 7219.7651 | 8255.3591 | $M/year |  | Total OpEx | 32902.6079 | 6562.6208 | 2718.1306 | $M/year |  | Total OpEx | 32902.6079 | 26341.0661 | 19779.5243 | 13217.9826 | 6656.4408 | $M/year |  | Total OpEx | 14971.2248 | 12258.7719 | 9546.319 | 6833.8661 | 4121.4132 | $M/year |  | Total OpEx | 6032.9656 | 5183.0079 | 4333.0502 | 3483.0925 | 2633.1348 | $M/year
Total Annual OpEx [$B] | 6.3563 | 7.2198 | 8.2554 | $B/year |  | Total Annual OpEx [$B] | 32.9026 | 6.5626 | 2.7181 | $B/year
Discount Rate | 10% | 10% | 10% |  |  | Discount Rate | 10% | 10% | 10%
5-year Total Cost | 71.8601 | 83.3508 | 96.7598 | $B |  | 5-year Total Cost | 362.7316 | 114.5118 | 70.3072 | $B |  | Output Comparison | [7 empty] | Output Comparison | [7 empty] | Output Comparison
10-year Total Cost | 86.8214 | 100.3445 | 116.1911 | $B |  | 10-year Total Cost | 440.1771 | 129.9588 | 76.7051 | $B |  | Launch Price | 4000 | 3000 | 2000 | 1000 | 0 | $/kg |  | Launch Price | 4000 | 3000 | 2000 | 1000 | 0 | $/kg |  | Launch Price | 4000 | 3000 | 2000 | 1000 | 0 | $/kg
20-year Total Cost | 101.8794 | 117.4481 | 135.748 | $B |  | 20-year Total Cost | 518.1233 | 145.5056 | 83.1443 | $B |  | ODC 20-year Total Cost | 518.1233 | 429.4535 | 340.7837 | 252.1139 | 163.444 | $B |  | ODC 20-year Total Cost | 259.1358 | 222.4809 | 185.826 | 149.1711 | 112.5162 | $B |  | ODC 20-year Total Cost | 127.9396 | 116.4536 | 104.9676 | 93.4817 | 81.9957 | $B
[6 empty] | ODC/TDC Total Cost Ratio | 5.0857 | 1.2389 | 0.61249 |  |  | TDC 20-year Total Cost | 101.8794 | 101.8794 | 101.8794 | 101.8794 | 101.8794 | $B |  | TDC 20-year Total Cost | 117.4481 | 117.4481 | 117.4481 | 117.4481 | 117.4481 | $B |  | TDC 20-year Total Cost | 135.748 | 135.748 | 135.748 | 135.748 | 135.748 | $B
[12 empty] | ODC Sensitivity Equation: Slope | 0.08867 | [6 empty] | ODC Sensitivity Equation: Slope | 0.036655 | [6 empty] | ODC Sensitivity Equation: Slope | 0.011486
Speed | [5 empty] | Speed | [5 empty] | ODC Sensitivity Equation: Y-intercept | 163.444 | [6 empty] | ODC Sensitivity Equation: Y-intercept | 112.5162 |  |  | Starship (Initial) | 145.5056 | $B |  | ODC Sensitivity Equation: Y-intercept | 81.9957
Time to Operations | 3 | 2 | 1.5 | years |  | Time to Operations | 11.2259 | 2.6081 | 0.058216 | years |  | Break-even launch cost | -694.3133 | [6 empty] | Break-even launch cost | 134.551 |  |  | Starship (Mature) | 116.1817 | $B |  | Break-even launch cost | 4679.8275
CapEx Breakdown and Comparison | [5 empty] | CapEx Breakdown and Comparison | [5 empty] | ODC/TDC Total Cost Ratio | 5.0857 | 4.2153 | 3.345 | 2.4746 | 1.6043 |  |  | ODC/TDC Total Cost Ratio | 2.2064 | 1.8943 | 1.5822 | 1.2701 | 0.95801 | $B |  | ODC/TDC Total Cost Ratio | 942478207.4745 | 857865874.9146 | 773253542.3547 | 688641209.7948 | 604028877.235 | $B
Tech Today | [5 empty] | Tech Today
Next Gen | [5 empty] | Next Gen
Future Concept | [5 empty] | Future Concept
CapEx Roadmap Progression | [5 empty] | CapEx Roadmap Progression
OpEx Breakdown and Comparison | [5 empty] | OpEx Breakdown and Comparison
Tech Today | [5 empty] | Tech Today
Next Gen | [5 empty] | Next Gen
Future Concept | [5 empty] | Future Concept
OpEx Roadmap Progression | [5 empty] | OpEx Roadmap Progression
Total Cost of Ownership
Tech Today - NPV
Next Gen - NPV
Future Concept - NPV
Roadmap Progression - NPV
Launch Cost Sensitivity

## Tabular Data for Plots (hidden)
Tech Today
|  | Terrestrial Data Center | [10 empty] | Orbital Data Center | [10 empty] | Comparison
# | Year | % Compute Online | CapEx | OpEx | DCF | Net Present Value | Latest GPU Generation | Do GPU Refresh? | Installed GPU Generation | TFLOP/GPU installed | EFLOPS of Data Center (FLOPS*10^18) | GFLOPS/NPV | % Compute Online | CapEx | OpEx | DCF | Net Present Value | Latest GPU Generation | Do GPU Refresh? | Installed GPU Generation | TFLOP/GPU installed | EFLOPS of Data Center (FLOPS*10^18) | GFLOPS/NPV | ODC efficiency difference TDC [GFLOPS/$]
1 | 2026 | 33.33% | 15921568627.451 | 2118764476.9601 | 18040333104.4111 | 18040333104.4111 | 1 | FALSE | 1 | 1979 | 517.3856 | 28.6794 | 8.333% | 19833737378.8888 | 2741883995.2304 | 22575621374.1192 | 22575621374.1192 | 1 | FALSE | 1 | 1979 | 129.3464 | 5.7295 | -80.02%
2 | 2027 | 66.67% | 15921568627.451 | 4237528953.9203 | 18326452346.7011 | 36366785451.1122 | 1 | FALSE | 1 | 1979 | 1034.7712 | 28.4537 | 16.67% | 19833737378.8888 | 5483767990.4607 | 23015913972.136 | 45591535346.2551 | 1 | FALSE | 1 | 1979 | 258.6928 | 5.6741 | -80.06%
3 | 2028 | 100% | 15921568627.451 | 6356293430.8804 | 18411456246.5549 | 54778241697.6671 | 2 | FALSE | 1 | 1979 | 1552.1569 | 28.3353 | 25% | 19833737378.8888 | 8225651985.6911 | 23189577987.2561 | 68781113333.5113 | 2 | FALSE | 1 | 1979 | 388.0392 | 5.6417 | -80.09%
4 | 2029 | 100% | 0 | 6356293430.8804 | 4775577333.4939 | 59553819031.161 | 2 | FALSE | 1 | 1979 | 1552.1569 | 26.0631 | 33.33% | 19833737378.8888 | 10967535980.9215 | 23141452561.8409 | 91922565895.3522 | 2 | FALSE | 1 | 1979 | 517.3856 | 5.6285 | -78.4%
5 | 2030 | 100% | 0 | 6356293430.8804 | 4341433939.5399 | 63895252970.701 | 3 | TRUE | 3 | 4452.75 | 3492.3529 | 54.6575 | 41.67% | 19833737378.8888 | 13709419976.1519 | 22910427808.9206 | 114832993704.2728 | 3 | TRUE | 3 | 4452.75 | 1455.1471 | 12.6719 | -76.82%
6 | 2031 | 100% | 0 | 6356293430.8804 | 3946758126.8545 | 67842011097.5554 | 3 | FALSE | 3 | 4452.75 | 3492.3529 | 51.4777 | 50% | 19833737378.8888 | 16451303971.3822 | 22530155882.4664 | 137363149586.7393 | 3 | FALSE | 3 | 4452.75 | 1746.1765 | 12.7121 | -75.31%
7 | 2032 | 100% | 0 | 6356293430.8804 | 3587961933.5041 | 71429973031.0595 | 4 | FALSE | 3 | 4452.75 | 3492.3529 | 48.892 | 58.33% | 19833737378.8888 | 19193187966.6126 | 22029681927.6906 | 159392831514.4298 | 4 | FALSE | 3 | 4452.75 | 2037.2059 | 12.781 | -73.86%
8 | 2033 | 100% | 0 | 6356293430.8804 | 3261783575.9128 | 74691756606.9723 | 4 | FALSE | 3 | 4452.75 | 3492.3529 | 46.7569 | 66.67% | 19833737378.8888 | 21935071961.843 | 21434003602.0271 | 180826835116.4569 | 4 | FALSE | 3 | 4452.75 | 2328.2353 | 12.8755 | -72.46%
9 | 2034 | 100% | 0 | 6356293430.8804 | 2965257796.2844 | 77657014403.2567 | 5 | FALSE | 3 | 4452.75 | 3492.3529 | 44.9715 | 75% | 19833737378.8888 | 24676955957.0734 | 20764566939.4785 | 201591402055.9355 | 5 | FALSE | 3 | 4452.75 | 2619.2647 | 12.9929 | -71.11%
10 | 2035 | 100% | 0 | 6356293430.8804 | 2695688905.7131 | 80352703308.9697 | 5 | TRUE | 5 | 10018.6875 | 7857.7941 | 97.7913 | 83.33% | 19833737378.8888 | 27418839952.3037 | 20039705508.1204 | 221631107564.0559 | 5 | TRUE | 5 | 10018.6875 | 6548.1618 | 29.5453 | -69.79%
11 | 2036 | 100% | 0 | 6356293430.8804 | 2450626277.921 | 82803329586.8907 | 6 | FALSE | 5 | 10018.6875 | 7857.7941 | 94.8971 | 91.67% | 19833737378.8888 | 30160723947.5341 | 19275029073.0466 | 240906136637.1025 | 6 | FALSE | 5 | 10018.6875 | 7202.9779 | 29.8995 | -68.49%
12 | 2037 | 100% | 0 | 6356293430.8804 | 2227842070.8372 | 85031171657.7279 | 6 | FALSE | 5 | 10018.6875 | 7857.7941 | 92.4107 | 100% | 19833737378.8888 | 32902607942.7645 | 18483767316.1835 | 259389903953.286 | 6 | FALSE | 5 | 10018.6875 | 7857.7941 | 30.2934 | -67.22%
13 | 2038 | 100% | 0 | 6356293430.8804 | 2025310973.4884 | 87056482631.2163 | 7 | FALSE | 5 | 10018.6875 | 7857.7941 | 90.2609 | 100% | 0 | 32902607942.7645 | 10483784873.6063 | 269873688826.8923 | 7 | FALSE | 5 | 10018.6875 | 7857.7941 | 29.1166 | -67.74%
14 | 2039 | 100% | 0 | 6356293430.8804 | 1841191794.0804 | 88897674425.2966 | 7 | FALSE | 5 | 10018.6875 | 7857.7941 | 88.3914 | 100% | 0 | 32902607942.7645 | 9530713521.4603 | 279404402348.3526 | 7 | FALSE | 5 | 10018.6875 | 7857.7941 | 28.1234 | -68.18%
15 | 2040 | 100% | 0 | 6356293430.8804 | 1673810721.8912 | 90571485147.1879 | 8 | TRUE | 8 | 33813.0703 | 26520.0551 | 292.808 | 100% | 0 | 32902607942.7645 | 8664285019.5094 | 288068687367.8619 | 8 | TRUE | 8 | 33813.0703 | 26520.0551 | 92.0616 | -68.56%
16 | 2041 | 100% | 0 | 6356293430.8804 | 1521646110.8102 | 92093131257.9981 | 8 | FALSE | 8 | 33813.0703 | 26520.0551 | 287.97 | 100% | 0 | 32902607942.7645 | 7876622745.0085 | 295945310112.8704 | 8 | FALSE | 8 | 33813.0703 | 26520.0551 | 89.6113 | -68.88%
17 | 2042 | 100% | 0 | 6356293430.8804 | 1383314646.1911 | 93476445904.1892 | 9 | FALSE | 8 | 33813.0703 | 26520.0551 | 283.7084 | 100% | 0 | 32902607942.7645 | 7160566131.8259 | 303105876244.6964 | 9 | FALSE | 8 | 33813.0703 | 26520.0551 | 87.4944 | -69.16%
18 | 2043 | 100% | 0 | 6356293430.8804 | 1257558769.2646 | 94734004673.4538 | 9 | FALSE | 8 | 33813.0703 | 26520.0551 | 279.9423 | 100% | 0 | 32902607942.7645 | 6509605574.3872 | 309615481819.0836 | 9 | FALSE | 8 | 33813.0703 | 26520.0551 | 85.6548 | -69.4%
19 | 2044 | 100% | 0 | 6356293430.8804 | 1143235244.786 | 95877239918.2399 | 10 | FALSE | 8 | 33813.0703 | 26520.0551 | 276.6043 | 100% | 0 | 32902607942.7645 | 5917823249.4429 | 315533305068.5264 | 10 | FALSE | 8 | 33813.0703 | 26520.0551 | 84.0484 | -69.61%
20 | 2045 | 100% | 0 | 6356293430.8804 | 1039304767.9873 | 96916544686.2272 | 10 | TRUE | 10 | 76079.4082 | 59670.1241 | 615.6856 | 100% | 0 | 32902607942.7645 | 5379839317.6754 | 320913144386.2018 | 10 | TRUE | 10 | 76079.4082 | 59670.1241 | 185.9385 | -69.8%
Next Gen
|  | Terrestrial Data Center | [10 empty] | Orbital Data Center | [10 empty] | Comparison
# | Year | % Compute Online | CapEx | OpEx | DCF | Net Present Value | Latest GPU Generation | Do GPU Refresh? | Installed GPU Generation | TFLOP/GPU installed | EFLOPS of Data Center (FLOPS*10^18) | GFLOPS/NPV | % Compute Online | CapEx | OpEx | DCF | Net Present Value | Latest GPU Generation | Do GPU Refresh? | Installed GPU Generation | TFLOP/GPU installed | EFLOPS of Data Center (FLOPS*10^18) | GFLOPS/NPV | ODC efficiency difference TDC [GFLOPS/$]
1 | 2031 | 50% | 27991099476.4398 | 3609882559.4663 | 31600982035.9061 | 31600982035.9061 | 1 | FALSE | 1 | 8400 | 2198.9529 | 69.585 | 33.33% | 29878100482.5728 | 2187540261.2081 | 32065640743.7809 | 32065640743.7809 | 1 | FALSE | 1 | 8400 | 1465.9686 | 45.7177 | -34.3%
2 | 2032 | 100% | 27991099476.4398 | 7219765118.9327 | 32009876904.8841 | 63610858940.7902 | 1 | FALSE | 1 | 8400 | 4397.9058 | 69.1377 | 66.67% | 29878100482.5728 | 4375080522.4162 | 31139255459.0809 | 63204896202.8618 | 1 | FALSE | 1 | 8400 | 2931.9372 | 46.3878 | -32.91%
3 | 2033 | 100% | 0 | 7219765118.9327 | 5966748032.1758 | 69577606972.966 | 2 | FALSE | 1 | 8400 | 4397.9058 | 63.2086 | 100% | 29878100482.5728 | 6562620783.6243 | 30116298567.105 | 93321194769.9668 | 2 | FALSE | 1 | 8400 | 4397.9058 | 47.1265 | -25.44%
4 | 2034 | 100% | 0 | 7219765118.9327 | 5424316392.8871 | 75001923365.8531 | 2 | FALSE | 1 | 8400 | 4397.9058 | 58.6372 | 100% | 0 | 6562620783.6243 | 4930594127.4412 | 98251788897.4081 | 2 | FALSE | 1 | 8400 | 4397.9058 | 44.7616 | -23.66%
5 | 2035 | 100% | 0 | 7219765118.9327 | 4931196720.8064 | 79933120086.6595 | 3 | TRUE | 3 | 18900 | 9895.288 | 123.7946 | 100% | 0 | 6562620783.6243 | 4482358297.6739 | 102734147195.0819 | 3 | TRUE | 3 | 18900 | 9895.288 | 96.3194 | -22.19%
6 | 2036 | 100% | 0 | 7219765118.9327 | 4482906109.824 | 84416026196.4835 | 3 | FALSE | 3 | 18900 | 9895.288 | 117.2205 | 100% | 0 | 6562620783.6243 | 4074871179.7035 | 106809018374.7854 | 3 | FALSE | 3 | 18900 | 9895.288 | 92.6447 | -20.97%
7 | 2037 | 100% | 0 | 7219765118.9327 | 4075369190.7491 | 88491395387.2326 | 4 | FALSE | 3 | 18900 | 9895.288 | 111.822 | 100% | 0 | 6562620783.6243 | 3704428345.185 | 110513446719.9704 | 4 | FALSE | 3 | 18900 | 9895.288 | 89.5392 | -19.93%
8 | 2038 | 100% | 0 | 7219765118.9327 | 3704881082.4992 | 92196276469.7318 | 4 | FALSE | 3 | 18900 | 9895.288 | 107.3285 | 100% | 0 | 6562620783.6243 | 3367662131.9864 | 113881108851.9568 | 4 | FALSE | 3 | 18900 | 9895.288 | 86.8914 | -19.04%
9 | 2039 | 100% | 0 | 7219765118.9327 | 3368073711.3629 | 95564350181.0947 | 5 | FALSE | 3 | 18900 | 9895.288 | 103.5458 | 100% | 0 | 6562620783.6243 | 3061511029.0785 | 116942619881.0353 | 5 | FALSE | 3 | 18900 | 9895.288 | 84.6166 | -18.28%
10 | 2040 | 100% | 0 | 7219765118.9327 | 3061885192.1481 | 98626235373.2428 | 5 | TRUE | 5 | 42525 | 22264.3979 | 225.7452 | 100% | 0 | 6562620783.6243 | 2783191844.6168 | 119725811725.6522 | 5 | TRUE | 5 | 42525 | 22264.3979 | 185.9616 | -17.62%
11 | 2041 | 100% | 0 | 7219765118.9327 | 2783531992.8619 | 101409767366.1047 | 6 | FALSE | 5 | 42525 | 22264.3979 | 219.5489 | 100% | 0 | 6562620783.6243 | 2530174404.1971 | 122255986129.8493 | 6 | FALSE | 5 | 42525 | 22264.3979 | 182.1129 | -17.05%
12 | 2042 | 100% | 0 | 7219765118.9327 | 2530483629.8745 | 103940250995.9792 | 6 | FALSE | 5 | 42525 | 22264.3979 | 214.2038 | 100% | 0 | 6562620783.6243 | 2300158549.2701 | 124556144679.1194 | 6 | FALSE | 5 | 42525 | 22264.3979 | 178.7499 | -16.55%
13 | 2043 | 100% | 0 | 7219765118.9327 | 2300439663.5222 | 106240690659.5014 | 7 | FALSE | 5 | 42525 | 22264.3979 | 209.5656 | 100% | 0 | 6562620783.6243 | 2091053226.6092 | 126647197905.7286 | 7 | FALSE | 5 | 42525 | 22264.3979 | 175.7986 | -16.11%
14 | 2044 | 100% | 0 | 7219765118.9327 | 2091308785.0202 | 108331999444.5216 | 7 | FALSE | 5 | 42525 | 22264.3979 | 205.52 | 100% | 0 | 6562620783.6243 | 1900957478.7356 | 128548155384.4642 | 7 | FALSE | 5 | 42525 | 22264.3979 | 173.1989 | -15.73%
15 | 2045 | 100% | 0 | 7219765118.9327 | 1901189804.5638 | 110233189249.0855 | 8 | TRUE | 8 | 143521.875 | 75142.3429 | 681.6671 | 100% | 0 | 6562620783.6243 | 1728143162.4869 | 130276298546.9511 | 8 | TRUE | 8 | 143521.875 | 75142.3429 | 576.7921 | -15.39%
16 | 2046 | 100% | 0 | 7219765118.9327 | 1728354367.7853 | 111961543616.8708 | 8 | FALSE | 8 | 143521.875 | 75142.3429 | 671.1442 | 100% | 0 | 6562620783.6243 | 1571039238.6245 | 131847337785.5756 | 8 | FALSE | 8 | 143521.875 | 75142.3429 | 569.9193 | -15.08%
17 | 2047 | 100% | 0 | 7219765118.9327 | 1571231243.4412 | 113532774860.3119 | 9 | FALSE | 8 | 143521.875 | 75142.3429 | 661.856 | 100% | 0 | 6562620783.6243 | 1428217489.6586 | 133275555275.2343 | 9 | FALSE | 8 | 143521.875 | 75142.3429 | 563.8119 | -14.81%
18 | 2048 | 100% | 0 | 7219765118.9327 | 1428392039.492 | 114961166899.8039 | 9 | FALSE | 8 | 143521.875 | 75142.3429 | 653.6324 | 100% | 0 | 6562620783.6243 | 1298379536.0533 | 134573934811.2876 | 9 | FALSE | 8 | 143521.875 | 75142.3429 | 558.3722 | -14.57%
19 | 2049 | 100% | 0 | 7219765118.9327 | 1298538217.72 | 116259705117.5239 | 10 | FALSE | 8 | 143521.875 | 75142.3429 | 646.3318 | 100% | 0 | 6562620783.6243 | 1180345032.7757 | 135754279844.0633 | 10 | FALSE | 8 | 143521.875 | 75142.3429 | 553.5173 | -14.36%
20 | 2050 | 100% | 0 | 7219765118.9327 | 1180489288.8363 | 117440194406.3603 | 10 | TRUE | 10 | 322924.2188 | 169070.2716 | 1439.6287 | 100% | 0 | 6562620783.6243 | 1073040938.887 | 136827320782.9503 | 10 | TRUE | 10 | 322924.2188 | 169070.2716 | 1235.647 | -14.17%
Future Concept
|  | Terrestrial Data Center | [10 empty] | Orbital Data Center | [10 empty] | Comparison
# | Year | % Compute Online | CapEx | OpEx | DCF | Net Present Value | Latest GPU Generation | Do GPU Refresh? | Installed GPU Generation | TFLOP/GPU installed | EFLOPS of Data Center (FLOPS*10^18) | GFLOPS/NPV | % Compute Online | CapEx | OpEx | DCF | Net Present Value | Latest GPU Generation | Do GPU Refresh? | Installed GPU Generation | TFLOP/GPU installed | EFLOPS of Data Center (FLOPS*10^18) | GFLOPS/NPV | ODC efficiency difference TDC [GFLOPS/$]
1 | 2036 | 50% | 32732752613.2404 | 4127679545.0182 | 36860432158.2587 | 36860432158.2587 | 1 | FALSE | 1 | 35600 | 6202.0906 | 168.2588 | 100% | 60003348678.3187 | 2718130563.0983 | 62721479241.417 | 62721479241.417 | 1 | FALSE | 1 | 35600 | 12404.1812 | 197.7661 | 17.54%
2 | 2037 | 100% | 32732752613.2404 | 8255359090.0365 | 37261919730.2517 | 74122351888.5104 | 1 | FALSE | 1 | 35600 | 12404.1812 | 167.3474 | 100% | 0 | 2718130563.0983 | 2471027784.6348 | 65192507026.0518 | 1 | FALSE | 1 | 35600 | 12404.1812 | 190.27 | 13.7%
3 | 2038 | 100% | 0 | 8255359090.0365 | 6822610818.212 | 80944962706.7224 | 2 | FALSE | 1 | 35600 | 12404.1812 | 153.2422 | 100% | 0 | 2718130563.0983 | 2246388895.1226 | 67438895921.1744 | 2 | FALSE | 1 | 35600 | 12404.1812 | 183.9322 | 20.03%
4 | 2039 | 100% | 0 | 8255359090.0365 | 6202373471.1018 | 87147336177.8241 | 2 | FALSE | 1 | 35600 | 12404.1812 | 142.3357 | 100% | 0 | 2718130563.0983 | 2042171722.8387 | 69481067644.0131 | 2 | FALSE | 1 | 35600 | 12404.1812 | 178.5261 | 25.43%
5 | 2040 | 100% | 0 | 8255359090.0365 | 5638521337.3653 | 92785857515.1894 | 3 | TRUE | 3 | 80100 | 27909.4077 | 300.7938 | 100% | 0 | 2718130563.0983 | 1856519748.0352 | 71337587392.0483 | 3 | TRUE | 3 | 80100 | 27909.4077 | 391.23 | 30.07%
6 | 2041 | 100% | 0 | 8255359090.0365 | 5125928488.5139 | 97911786003.7033 | 3 | FALSE | 3 | 80100 | 27909.4077 | 285.0465 | 100% | 0 | 2718130563.0983 | 1687745225.4865 | 73025332617.5349 | 3 | FALSE | 3 | 80100 | 27909.4077 | 382.188 | 34.08%
7 | 2042 | 100% | 0 | 8255359090.0365 | 4659934989.5581 | 102571720993.2614 | 4 | FALSE | 3 | 80100 | 27909.4077 | 272.0965 | 100% | 0 | 2718130563.0983 | 1534313841.3514 | 74559646458.8863 | 4 | FALSE | 3 | 80100 | 27909.4077 | 374.3232 | 37.57%
8 | 2043 | 100% | 0 | 8255359090.0365 | 4236304535.9619 | 106808025529.2232 | 4 | FALSE | 3 | 80100 | 27909.4077 | 261.3044 | 100% | 0 | 2718130563.0983 | 1394830764.8649 | 75954477223.7512 | 4 | FALSE | 3 | 80100 | 27909.4077 | 367.4491 | 40.62%
9 | 2044 | 100% | 0 | 8255359090.0365 | 3851185941.7835 | 110659211471.0068 | 5 | FALSE | 3 | 80100 | 27909.4077 | 252.2104 | 100% | 0 | 2718130563.0983 | 1268027968.059 | 77222505191.8102 | 5 | FALSE | 3 | 80100 | 27909.4077 | 361.4155 | 43.3%
10 | 2045 | 100% | 0 | 8255359090.0365 | 3501078128.8941 | 114160289599.9009 | 5 | TRUE | 5 | 180225 | 62796.1672 | 550.0701 | 100% | 0 | 2718130563.0983 | 1152752698.2355 | 78375257890.0456 | 5 | TRUE | 5 | 180225 | 62796.1672 | 801.2244 | 45.66%
11 | 2046 | 100% | 0 | 8255359090.0365 | 3182798298.9947 | 117343087898.8955 | 6 | FALSE | 5 | 180225 | 62796.1672 | 535.1501 | 100% | 0 | 2718130563.0983 | 1047956998.3959 | 79423214888.4415 | 6 | FALSE | 5 | 180225 | 62796.1672 | 790.6525 | 47.74%
12 | 2047 | 100% | 0 | 8255359090.0365 | 2893452999.086 | 120236540897.9816 | 6 | FALSE | 5 | 180225 | 62796.1672 | 522.2719 | 100% | 0 | 2718130563.0983 | 952688180.3599 | 80375903068.8014 | 6 | FALSE | 5 | 180225 | 62796.1672 | 781.281 | 49.59%
13 | 2048 | 100% | 0 | 8255359090.0365 | 2630411817.351 | 122866952715.3325 | 7 | FALSE | 5 | 180225 | 62796.1672 | 511.0908 | 100% | 0 | 2718130563.0983 | 866080163.9635 | 81241983232.7649 | 7 | FALSE | 5 | 180225 | 62796.1672 | 772.9522 | 51.24%
14 | 2049 | 100% | 0 | 8255359090.0365 | 2391283470.319 | 125258236185.6516 | 7 | FALSE | 5 | 180225 | 62796.1672 | 501.3336 | 100% | 0 | 2718130563.0983 | 787345603.6032 | 82029328836.3681 | 7 | FALSE | 5 | 180225 | 62796.1672 | 765.5331 | 52.7%
15 | 2050 | 100% | 0 | 8255359090.0365 | 2173894063.9264 | 127432130249.578 | 8 | TRUE | 8 | 608259.375 | 211937.0645 | 1663.1368 | 100% | 0 | 2718130563.0983 | 715768730.5484 | 82745097566.9165 | 8 | TRUE | 8 | 608259.375 | 211937.0645 | 2561.3247 | 54.01%
16 | 2051 | 100% | 0 | 8255359090.0365 | 1976267330.8422 | 129408397580.4202 | 8 | FALSE | 8 | 608259.375 | 211937.0645 | 1637.7381 | 100% | 0 | 2718130563.0983 | 650698845.9531 | 83395796412.8696 | 8 | FALSE | 8 | 608259.375 | 211937.0645 | 2541.3399 | 55.17%
17 | 2052 | 100% | 0 | 8255359090.0365 | 1796606664.402 | 131205004244.8222 | 9 | FALSE | 8 | 608259.375 | 211937.0645 | 1615.3124 | 100% | 0 | 2718130563.0983 | 591544405.4119 | 83987340818.2814 | 9 | FALSE | 8 | 608259.375 | 211937.0645 | 2523.4406 | 56.22%
18 | 2053 | 100% | 0 | 8255359090.0365 | 1633278785.82 | 132838283030.6422 | 9 | FALSE | 8 | 608259.375 | 211937.0645 | 1595.4517 | 100% | 0 | 2718130563.0983 | 537767641.2835 | 84525108459.565 | 9 | FALSE | 8 | 608259.375 | 211937.0645 | 2507.3859 | 57.16%
19 | 2054 | 100% | 0 | 8255359090.0365 | 1484798896.2 | 134323081926.8421 | 10 | FALSE | 8 | 608259.375 | 211937.0645 | 1577.8157 | 100% | 0 | 2718130563.0983 | 488879673.8941 | 85013988133.4591 | 10 | FALSE | 8 | 608259.375 | 211937.0645 | 2492.967 | 58%
20 | 2055 | 100% | 0 | 8255359090.0365 | 1349817178.3636 | 135672899105.2058 | 10 | TRUE | 10 | 1368583.5938 | 476858.395 | 3514.7653 | 100% | 0 | 2718130563.0983 | 444436067.1765 | 85458424200.6356 | 10 | TRUE | 10 | 1368583.5938 | 476858.395 | 5580.0045 | 58.76%

## TDC Metrics
© 2026 Technology Strategy Partners ¦ All rights reserved.
Terrestrial Data Center - Research and Metrics Rationale
Key Inputs Metrics - Technology State Estimation
Metric |  | Tech Today | Next Gen | Future Concept | Rationale / Confidence
PUE |  | 1.3 | 1.1 | 1.05 | Most new data centers today are 1.3, Google is already at 1.1 (assume standard for next gen), and future limits should exceed today's best state.
Electricity Price ($/kWh) |  | 0.06 | 0.08 | 0.1 | $0.06/kWh is pretty standard today; assuming upward trend in the future and neglecting potential behind-the-meter solutions.
Non-GPU IT Hardware CapEx (% of GPU $) |  | 52% | 52% | 52% | Fairly conservative estimate today; future values are uncertain due to market forces, but likely balances out due to CPU cost reduction and RAM cost increase
Network & Software Scale ($/W/year) |  | 0.36 | 0.36 | 0.36 | Estimate grounded in today's general consensus; history suggests these costs remain flat or deflate ain real terms over time, safe to assume 0% CAGR net inflation.
WUE (L/kWh) |  | 1.8 | 0.2 | 0 | Industry average today is 1.8, but current closed-loop systems exhibit 0.2. Physical limit is 0.
Water Price ($/gallon) |  | 0.00613 | 0.00711 | 0.00824 | Industry average today $6.13/1000 gallons; official federal estimate calculator informs future prices.
Powered Shell Scale ($/W) |  | 12 | 14.6 | 17.8 | Conservative today; assumes trends of costs continue on current trajectory
Maintenance & Staffing OpEx Scale ($/W/year) |  | 0.36 | 0.36 | 0.36 | Estimate grounded in today's general consensus; official guidance is that this tracks with inflation, meaning 0% CAGR net inflation.
Property Taxes ($/W/yr) |  | 0.17 | 0.21697 | 0.27691 | Estimate grounded in multiple sources; history suggests a 5% real CAGR
Permitting, Construction, & Commissioning Time (years) |  | 3 | 2 | 1.5 | Assumes no major supply chain bottlenecks, more behind-the-meter generation alleviates connection queue times, and modular construction speeds up the process.
Metric: Power Usage Effectiveness (PUE)
Google 2025 Environmental Report
2025 Environmental Report (2024 data)
"The average annual power usage effectiveness (PUE) for our global fleet of data centers dropped below 1.10 to 1.09"
84% less overhead than industry average (1.56)
Globally consumed 8.1 billions gallons of water across data centers
Equinix 2024 Sustainability Data Summary
"Reached 96% of renewable energy coverage"
"Achieved an annual average global PUE of 1.39"
"Achieved 0.95 average annual Water Usage Effectiveness (WUE) for our entire global portfolio of data centers"
Uptime Institute Global Data Center Survey 2024
"Average PUE levels remain mostly flat for the fifth consecutive year, but this obscures advances in newer, larger facilities."
"In the 2024 survey results, the industry average PUE [is] 1.56"
Significant drop over the last 20 years but flattening out
"Many recent builds consistently achieve a PUE of 1.3 - and sometimes much better"
Metric: Electricity Price ($/kWh)
US Energy Information Administration
The US national average industrial electricity price in 2024 was $0.0813/kWh
"Industrial" rate is an average across all industrial consumers; data centers may be able to negotiate better rates.
PVTech
US solar PPA prices climb to $61.67/MWh
$0.06167/kWh
Greening (report)
ERCOT - still the most competitive region for solar PPAs
Average prices ranging from $35-45/MWh
$0.035-$0.045/kWh
Let's assume $0.06/kWh for a conservative scenario today.
The trend is upward in the near term, let's assume $0.08/kWh for Next Gen
Future Limits are uncertain considering potentially better behind-the-meter power supplies, but let's assume $0.10/kWh from the grid.
Metric: Non-GPU Hardware CapEx
Alpha-Matica
"Total IT Equipment estimated at $2.5-$4B for 100 MW facility with 100,000 GPUs"
This doesn't exactly line up with my model - a 100 MW facility is ~78,000 H100 GPUs
Likely a difference in GPU selection
78,000 H100 GPUs cost rough $2.5B
Conservatively, $4B total IT - $2.5B for GPUs = $1.5B for non-GPU IT hardware CapEx max
This equates to roughly 60% of GPU spend
Bernstein analysis
GPUs represent 39% of total CapEx
Networking + CPUs + Storage are roughly 17% of total CapEx
17/39=44% of GPU spend
Semianalysis
GPUs account for 65.8% of Meta's H100 cluster. Includes integration and much more.
Remaining IT equipment is 34.2%
IT proportion is 34.2/65.8=52%
--->The average of these three is 52%.
We expect this number to scale directly with GPU cost (and performance), therefore, will remain flat over time horizons
Competing downward pressure on CPUs but upward pressure on RAM balance prices out
TDC OpEx Metrics
Note: There is very little information on TDC OpEx that is publicaly available. In general, these are proprietary.
The breakdowns and scope between sources are mixed; we had to estimate how these different sources may align.
Alpha-Matica
OpEx Breakdown for a 100 MW Facilitiy (see source for detailed description):
|  | Category |  |  | Low-end $/W | High-end $/W | Avg $/W | % OpEx
|  | Electricity |  |  | 0.41 | 1.31 | 0.86 | 11.24%
|  | Hardware refresh |  |  | 4.17 | 8 | 6.09 | 79.61%
|  | Infrastructure maintenance |  |  | 0.1 | 0.25 | 0.18 | 2.353%
|  | Staffing & Human Resources |  |  | 0.1 | 0.25 | 0.18 | 2.353%
|  | Network & Bandwidth |  |  | 0.1 | 0.25 | 0.18 | 2.353%
|  | Software, Security & Compliance |  |  | 0.1 | 0.25 | 0.18 | 2.353%
|  | Total |  |  |  |  | 7.65
In the model, we account for hardware refresh as a separate line item. Therefore, subsystem OpEx breakdown might look more like:
|  | Category |  |  | Avg $/W | % Opex | Where this might fit in
|  | Electricity |  |  | 0.86 | 54.43% | Power
|  | Infrastructure maintenance |  |  | 0.18 | 11.39% | Deployment
|  | Staffing & Human Resources |  |  | 0.18 | 11.39% | Deployment
|  | Network & Bandwidth |  |  | 0.18 | 11.39% | Compute
|  | Software, Security & Compliance |  |  | 0.18 | 11.39% | Compute
|  | Total |  |  | 1.58
Consolidated subsystem OpEx breakdown could be:
|  | Subsystem | OpEx | Units | Scope
|  | Power | 0.86 | $/W | Cost of power
|  | Compute | 0.36 | $/W | Network, software, compliance
|  | Deployment | 0.36 | $/W | Infrastructure maintenance, staffing
Thunder Said Energy
Assumes 30 MW data center base case
Does not give scale without buying the paper
OpEx Breakdown:
|  | Category |  |  |  | % OpEx | Cross-check Alpha-Matica
|  | Maintenance |  |  |  | 40% | 81.96% |  |  | Amortized hardware refresh is highly variable, could contribute to this difference
|  | Electricity |  |  |  | 20% | 11.24%
|  | Everything else (labor/water/G&A/other) |  |  |  | 40% | 7.059%
--> does not line up very well
Uptime Institute 2024 Data Center Spending Survey
Generic data center numbers
OpEx Breakdown:
|  | Category |  |  |  |  | % OpEx | Cross-check Alpha-Matica
|  | Power |  |  |  |  | 17% | 55%
|  | Maintenance |  |  |  |  | 17% | 11%
|  | Labor |  |  |  |  | 16% | 11%
|  | Space (capital repayments, rent, property taxes) |  |  |  |  | 16% |  |  |  | Dependent on financing situation
|  | Bandwidth |  |  |  |  | 16% | 11%
|  | Other |  |  |  |  | 15% | 11%
What can we do here?
Power is very dependent on usage, so we can calculate that separately
Amortized hardware refresh dependent on hardware cost and time scale, so we calculate that separately
Capital repayment/rent depending on financing structure - we exclude this type of ongoing cash flow from OpEx (in CapEx)
We need to add in property taxes
We're left with:
|  | Category |  |  | Alpha-Matica ratio | Alpha-Matica $/W | Thunder Said Category |  | Uptime Institute (excluding capital repayments)
|  | Infrastructure Maintenance |  |  | 25% | 0.18 | Maintenance |  | 25%
|  | Staffing & Human Resources |  |  | 25% | 0.18 | Everything else |  | 25%
|  | Network & Bandwidth |  |  | 25% | 0.18 | Everything else |  | 25%
|  | Software, Security, & Compliance |  |  | 25% | 0.18 | Could be maintenance |  | 25%
|  | Total |  |  | 100% | 0.72
---> It seems there is a case here that these categories are roughly equally split and they can be scaled via the Alpha-Matica $/W breakdown
The breakdown itself is less important, but alignment (or rough alignment) between sources indicates the data is starting to converge.
$/W total OpEx is most important; breakdown is used to model technical progression over time
Furthermore, we can simplify these into:
|  | Category |  | Ratio | $/W | Subsystem | Scope
|  | Maintenance & Staffing |  | 50% | 0.36 | Deployment | Preventative maintenance for power/cooling/building + staff
|  | Network & Software |  | 50% | 0.36 | Compute | Connectivity, software licensing, cybersecutiy, regulatory compliance
All numbers are on a per year basis
US FEMP Guidance on Utility Rate Estimations
For non-energy O&M costs (labor, repair parts, maintenance, the guidance states:
"In these cases, in the absence of compelling evidence to the contrary, the long-term general inflation rate as forecast by the President's Council of Economic Advisers (CEA), as found in NIST's current EERC tool, is a logical escalator."
Meaning, the official recommendation is that O&M costs escalate at the general inflation rate - net of inflation that is 0% CAGR.
BLS Producer Price Index by Industry: Software Publishers
Jan 2026 index value: 97.558; Dec 2025: 101.327; Oct 2025: 102.852; Sep 2025: 99.746
The index has gone down from 100 (Dec 1997) to 97.6 (Jan 2026) over 28 years - a nominal decline of 2.4%.
US CPI rose roughly 80-85% over the same period, meaning software prices have actually fallen substantially in real terms, ~2-3% CAGR
BLS Producer Price Index by Industry: Data Processing, Hosting and Related Services
Sep 2025 index value: 123.930; Aug 2025: 124.910; Jul 2025: 126.753; Jun 2025: 123.663
The index has gone from 100 (Dec 2000) to 123.9 (Sep 2025) over ~25 years - a nominal increase of 24%, or roughly 0.9% CAGR
US CPI rose roughly 75-80% over the same period, meaning data processing and hosting service prices have also declined in real terms, ~2.5-2% CAGR
The two BLS sources indicate:
Prices have been flat or declining in nominal terms over 25+ years; meaningfully deflationary in real terms
Therefore, it is conservative to assume 0% real growth (net inflation) in the software/network category.
Metric: Water Usage Effectiveness (WUE; gallon/kWh)
AWS 2024 Sustainability Report
AWS achieved a global data center WUE of 0.15 liters of water withdrawn per kWh of IT load in 2024, a 17% improvement from 2023 and 40% improvement since 2021
AWS is committed to being water positive by 2030; returning more water to communities than we use in direct operations
Cologix closed-loop liquid cooling systems
"In 2024, Cologix achieved an average WUE of 0.203 across its facilities, far below the industry average of 1.8."
Lawrence Barkeley National Laboratory
US fleet-wide average (air and liquid cooled included)
Average WUE is expected between 0.45 and 0.48 L/kWh
Environmental and Energy Study Institute
"The average WUE across data centers is 1.9 L/kWh"
Given the numbers vary widely for data centers (a mix of architectures), we'll take a conservative 1.8 L/kWh for today's value
Next Gen (closed-loop) solutions could hit 0.2 L/kWh if Cologix's architecture is widely adopted
Future Limits means an ideal 0 L/kWh - fully enclosed and recycled water system.
Metric: Water Price ($/gallon)
US Environmental Protection Agency
Commercial cost of water, national average: $6.13/1000 gallons
US Federal Energy Management Program (FEMP) Guidance on Utility Rate Estimations
"Maximum real (or net-of-inflaiton) compound annual escalation rates should be capped at 3.0% for water supply"
Using these two extremely authoritative sources, water prices should follow the trend:
Today: $6.13 / 1000 gallons
Next Gen (5 years): $7.11 / 1000 gallons
Future Limits (10 years): $8.24 / 1000 gallons
Metric: Powered Shell Scale ($/W)
Key Terms
Cold shell: just the building - structure, roof, walls, floow. No mechanical or electrical systems installed. Basically the core/shell bucket alone.
Warm shell: building plus partial electrical/mechanical infrastructure - maybe some power equipment and base building HVAC, but not the full redundant power chain or cooling equipment. Ready for a tenant to finish the fit-out.
Powered shell / turn-key (minus IT): everything needed to accept IT equipment - full redundant power chain from utility to rack, full cooling plant, fire suppression, monitoring.
JLL 2026 Global Data Center Outlook
"Power, not location or cost, will be the primary site selection criteria due to multiyear wait times for a grid connection."
"Nearly 100 GW of new data centers will be added between 2025 and 2030, doubling global capacity"
"AI could represent half of data center workloads by 2030"
"A significant shift is anticipated in 2027, when inference workloads could overtake training as the dominate AI requirement"
"Data centers turn to on-site power and battery storage"
"Between 2020 and 20205, the average global data center construction cost increased from $7.7 to $10.7 million per MW, equating to 7% CAGR. For 2026, JLL is forecasting the average global cost will crease 6% to $11.3 million per MW."
"These figures only include the cost to construct the shell and core. Tenants are typically responsible for the tech fit-out which can cost as much as $25 million per MW for AI infrastructure"
"3 trillion investment required for 100 GW of new supply by 2030"
Turner & Townsend 2025-2026 Data centre construction cost index
"Data was captured from more than 300 live or recent projects in more than 20 countries."
"Construction cost data is captured under the following key capital cost headings:
shell and core
architectural fit-out and finishes
mechanical and electrical fit-out
general contractor preliminaries
general contractor margin
general contractor contingency
mechanical and electrical equipment
"The cost model does not include any client direct costs, land purchase costs, utility works, abnormal groundworks, site works, active IT equipment, fibre capbling to support office fit-outs or professional services fees."
"Stabilization for traditional data centres, while AI costs are still to be fully determined."
"Data centre construction costs are set to climb modestly through 2026."
"Our data centre construction cost index for 2025 shows a 5.5% increase in the cost per watt of building a traditional cloud-based, air-cooled data center. This is markedly lower than the 9.0% YoY increase in 2024."
AI constuction premium: They estimate that "average construction costs are 7 to 10% higher than equivalent air-cooled data centres."
Breakdown:
|  |  | Cateogry |  |  |  | Air-cooled | Liquid-cooled
|  |  | CG/GRs and GC fees (ie preliminaries) |  |  |  | 10% | 10%
|  |  | Core/shell and architectural |  |  |  | 14% | 9%
|  |  | Mechanical (incl. equipment) |  |  |  | 22% | 33%
|  |  | Electrical (incl. equipment) |  |  |  | 54% | 48%
|  |  | Total |  |  |  | 100% | 100%
GC = General Contractor; GRs = General Requirements; contractor's overhead for managing the project; cost of having someone run the build
Core/shell and architectural: the building itself; foundations, walls, interior, loading docks, architectural finishes; smaller for liquid-cooled because higher power density means a smaller building footprint
Mechanical: cooling plant (chillers, coolant distribution, direct-to-chip loops, manifolds), also includes general HVAC, fire suppresion, and plumbing
Electrical: switchgear, transformers, UPS, backup generators, PDUs, cabling/conduit. Everything from utility to rack-level power.
This breakdown does not account for:
IT hardware - GPUs, servers, CPUs, memory, and networking; "active IT equipment"
Land
Utility works - the grid interconnection, substation upgrades, or on-site power generation if applicable
Many prices per W listed in one of the charts, a few examples:
Silicon Valley $13.31/W
Chicago $11.23/W
Atlanta $9.90/W
Dgtl Infra article: How Much Does it Cost to Build a Data Center? (2023)
Industry blog/newsletter; not a consulting firm, not a research house with proprietary datasets
Their data center cost article is one of the most-cited pieces in the space
Their cost breakdown does not cite a primary source; it appears synthesized from publicly available operator disclosures and industry convention.
Their operator specific figures are derived from SEC filings and earnings disclosures
Can likely trust the $M/MW scale figures but take the breakdown with a grain of salt.
"As a general rule, it costs between $600-$1,100 per gross square foot or $7-$12M/MW of commissioned IT load to build a data center."
"…generally broken down into four main categories:"
1. Land and building shell (15-20%): building shell, raised floor
2. Electrical Systems (40-50%): electrical backup generator, batteries, PDU, UPS, switchgear/transformers
3. HVAC/Mechanical/Cooling (15-20%): computer room air conditioner (CRAC), computer room air handler (CRAH), chillers, pipes
4. Building Fit-out (20-25%): lobby/entrance, rooms, shipping & receiving area
"Data center equipment…all have useful lives of 20+ years"
"Scale [of the data center, MW] provides a build cost advantage"
The bigger the MW, the more economies of scale
"In terms of the powered shell, land costs range between $25 to $75 per gross sqft, while the building shell costs between $80 to $160 per gross sqft"
"As such, the total powered shell costs range between $105 to $235 per gross sqft, equivalent to 17% to 21% of total development costs."
"Total develop costs for a greenfield data center typically range from $7-12M/MW of commissioned IT load."
Four key areas where customer (data center) requirements differ, impacting building costs: power density, redundancy, scale, timing
Key Takeaways
Based on the above sources, it is reaonsable to assume the cost of a modern AI data center to be somewhere in the $10-12M/MW (IT Load) range. Includes:
Land
Building
Mechanical
Electrical
Excludes all GPU and necessary racks/networking/CPUs
Since AI data centers tend to cost on the upper end of that spectrum, let's assume $12M/MW conservatively.
As data centers grow in size, this $/W value tends to decrease, though the exact relationship remains unknown.
The overall cost of data centers tend to increase at a 7% CAGR
For a Next-Gen facility (starting in 5 years), the cost scale comes to $16.8/W not accounting for inflation
In today's dollars (assuming a 3% interest rate), this comes to $14.6/W
For a Future Limits facility (starting in 10 years), the cost scale comes to $23.6/W - nearly double today
In today's dollars (assuming a 3% inflation rate), this comes to $17.8/W
Metric: Property Taxes
US Chamber of Commerce
"Property taxes are estimated to be… about 12% of annual operating spending"
Utilizing this model to compute OpEx, this comes out to be roughly $0.17/W/yr
This matches the relative scale in the Uptime Institute source.
Prince William County (Virginia) tax history
Rateswere frozen from 2012 to 2019, then increased over subsequent years.
The rate trajectory was ~24% CAGR over this five year increase, but likely playing catch-up from previous freeze.
CAGR over the 13 year period was 9.76%
This represents a real CAGR post-inflation of approximately 6.96%
Some of this increase may be playing catch-up for lost cash flow, meaning we could assume some nominal lower rate, say 5%
Metric: Development Times
Datacenters . Com
"In the past, securing permits for a new data center might have taken 6-12 months. Today, in markets like Northern Virginia, Dublin, and Singapore, the process can stretch into 2-3 years."
This is for permitting alone - land use, environmental, noise, building permits.
This is highly dependent on market.
Bain & Company
"Equipment lead times ranging from eight to 24 months. Skilled-labor shortages add further strain, but the most challenging of all is electricity utility connection with delays of up to five years."
Utility interconnection - not construction, not permitting - is the longest single item. Up to 5 years for grid connection in constrained markets.
Compute Forecast
"Constructing high-voltage transmission lines, the backbone for delivering large loads, often requires five to seven years."
"Studies can take 12 to 24 months or more, particularly when multiple developers compete for limited capacity."
If new transmission is required, you're looking at 5-7 years just for the power delivery infrastructure.
Campus Energy
"In Texas, CenterPoint Energy reported a 700% increase in large load interconnection requests, growing 1 GW to 8 GW between late 2023 and late 2024."
Queue congestion is worsening, not improving, which means these delays are likely to persist or grow in the near term.
Epoch AI
"the time from starting construction to achieving 1 GW of total facility power ranges from 1 to 3.6 years, with xAI projecting just 12 months to build Colossus 2."
Crusoe / Stargate Abilene
"Construction of the multi-building campus began in June 2024"
~15 months from construction start to first phase energized (200 MW). Second phase (adding 1 GW more) started March 2025, expected energized mid-2026; roughly another 15 months
Epoch AI
"We assume a default 150-day lag from building roof completion and this milestone, which reflects the typical time required for interior fit-out, rack installation, and network integration."
~5 months for commissioning after building copletion
Network Installers
Commissioning specialists are locked into builds 12-18 months in advance
In summary
| Phase |  |  |  | Typical Range
| Permitting |  |  |  | 6-36 months
| Power procurement /grid interconnect |  |  |  | 12-60+ months
| Construction |  |  |  | 12-24 months
| Commissioning |  |  |  | 3-6 months
| Total |  |  |  | 3 years |  | often cited today as the typical timeline
5-year horizon
Several forces are pulling in both directions.
Faster:
modular/prefabricated approaches are reducing schedule by 30-50%
FERC reforms are streamlining queue processing
Learning curves are improving building design
Slower/unchanged:
Grid infrastructure buildout is physically slow
Interconnection requests have surged 700% in some markets, and queue reforms are only showing "early signs of promise"
Transformer and switchgear lead times remain multi-year. Gas turbine order backlogs…
Estimate:
Construction phase compresses to 10-18 months
Permitting may ease modestly (2-3 years --> 1-2 years)
Power remains bottleneck, but on-site generation partially mitigates this
Total: 2 years
10-year horizon
This is more speculative and generally assumes the industry gets better at building data centers, not worse.
Many behind-the-meter solutions may eliminate the power procurement side of things.
Modular construction should be fully mature.
But community opposition may become stronger.
Estimate: 1.5 years

## Compute Metrics
© 2026 Technology Strategy Partners ¦ All rights reserved.
GPU Stats - Shared between TDC and ODC
Key Input Metrics - Technology State Estimation
Metric | Tech Today | Next Gen | Future Concept | Rationale / Confidence
GPU Selection | H100 SXM | Estimated (5-year) | Estimated (10-year)
Unit Cost ($/GPU) | 30000 | 52000 | 90000 | roughly 23%/yr launch price CAGR but moderated
GPU TDP (W) | 700 | 1050 | 1580 | 8.5%/yr CAGR
GPU Average Power % | 80% | 80% | 80% | No trend data, hold constant
Effective Rated Design Power (W/GPU) | 1275 | 1910 | 2870 | ~8.5%/yr (tracks TDP)
GPU Performance (TFLOPS) | 1979 | 8400 | 35600 | FLOPS/W 2yr doubling × TDP growth
Physical Replacement Rate (%/year) | 0.8% | 0.8% | 0.8% | No trend data, hold constant
Mass (kg) | 1.5 | 2 | 2.8 | ~6%/yr estimate; least confidence
TFLOPS/W | 2.83 | 8 | 22.5 | 2-year doubling
Most GPU metrics can be found in the H100 Datasheet
Metric : GPU Failure Rate
NCSA Delta H100
608 H100 GPUs over exactly 146 days; exactly 2 physical replacements after row-remapping exhausted (92 % of uncorrectable errors recovered without swap)
Strongest direct SRE observation. Gold-standard primary data. Must equate to GPU-hours/year for failure rate
-->0.82%/year
Cyfuture Cloud Production Fleet
Aggregate commercial H100 fleet under sustained workloads
Independent operator benchmark matching NCSA. Must equate to GPU-hours/year for failure rate
~0.8%/year
Meta Llama 3 405B (upper-bound inference)
16 384 H100s over 54 days; only 3 manual interventions out of 419 interruptions
Primary hyperscaler data. Conservative ground-based estimate. Must equate to GPU-hours/year for failure rate.
~0.12%/year
Growth in Other GPU Metrics
FLOPS/W efficiency
Epoch AI
"The energy efficiency of leading GPUs and TPUs has doubled every 2 years" in tensor-FP16 format
A broader academic study found FLOPS/W doubles around every 3-4 years across 4,000+ GPU models.
The faster 2-year doubling applies to frontier ML accelerators specifically; the 3-4 year rate is the broader GPU popultion
FLOPS/$ price-performance
Epoch AI
"The amount of floating-point operations/second per $ doubles every ~2.5 years" across 470 GPU models
TDP growth
arXiv paper
"the TDP of the selected NVIDIA GPUs grew by a much slower 8.5% every year" from 171W (Tesla C870, 2007) to 1,100W (B300, 2025)
GPU launch price grew at "22.9% CAGR from 2007 to 2025"
Applying these to the input metrics…
GPU TDP (W) grows by 8.5%/yr CAGR
GPU Performance FP8 (TFLOPS) 2 year doubling * TDP growth
TFLOPS/W : 2-year doubling
Eff. Rated Design Power : ~8.5%/yr (tracks TDP)
Unit Cost ($/GPU) : 23%/yr launch price CAGR
Mass (kg) : ~6%/year estimate (no published trend rate; directionally up due to more transistors, stacks, thermal solutions)

## ODC Metrics
© 2026 Technology Strategy Partners ¦ All rights reserved.
Orbital Data Center - Research and Metrics Rationale
Key Input Metrics - Technology State Estimation
Metric |  |  |  | Tech Today | Next Gen | Future Concept | Rationale / Confidence
Solar Specific Cost ($/W) |  |  |  | 50 | 29.62 | 15 | Sufficient vertical integration + economies of scale + advances in manufacturing techniques
Solar Specific Mass (kg/W) |  |  |  | 0.010417 | 0.0033003 | 0.00033333 | Associated with trajectory of solar technology
Radiator Operating Temp (K) |  |  |  | 350 | 400 | 500 | Demands new technology paradigm
Effective Emissivity ε |  |  |  | 0.91 | 0.95 | 0.97 | Demands new technology paradigm
Radiator Mass Density (kg/m²) |  |  |  | 6 | 5 | 4 | Good R&D can produce the most efficient design here
Radiator Cost Density ($/m²) |  |  |  | 210 | 189 | 170 | Likely poor accuracy in these numbers, but likely in the right order-of-magnitude
Integration Systems Mass Factor |  |  |  | 40.9% | 40.9% | 40.9% | Somewhat confident in these; values based in well-regarded SMAD textbook. These are fairly "sticky" integration factors that don't change much, but could be optimized over several iterations.
Integration Systems Cost Factor |  |  |  | 30% | 25% | 20% | Likely poor accuracy in these numbers, but likely in the right order-of-magnitude
Payload to Orbit (kg) |  |  |  | 17500 | 100000 | 200000 | F9 --> Starship (Initial) --> Starship (Mature)
Price per Launch |  |  |  | 70000000 | 90000000 | 20000000 | F9 --> Starship (Initial) --> Starship (Mature)
Launch Rate (launch/year) |  |  |  | 167 | 52 | 365 | F9 --> Starship (Initial) --> Starship (Mature)
Constellation Operations Cost ($/year) |  |  |  | 250000000 | 250000000 | 250000000 | Flat estimate bounded by Iridium ($178M/yr) and Starlink (~$300-500M/yr) analogs; no end-user ops.
Metric: Solar Specific Cost ($/W) & Solar Specific Mass (kg/W)
QYResearch
"Multi-junction cells cost 50-100x per watt compared to terrestrial silicon"
"Critical question: can III-V space cells achieve $100-200/W? Not in this decade."
"Can they achieve $300-400/W at constellation scale? Yes, and this is the procurement battleground."
Nanowerk
"Panels… rank among the most expensive components onboard."
"The gallium arsenide cells that dominate space power are grown atom by atom in high-vacuum chambers from scarce materials."
"After recent cost reductions driven by mega-constellation demand, space-grade cells still run between $50-150 per watt."
"Terrestrial silicon panels, by contrast, now sell for under $0.30 per watt
"That gap of two to three orders of magnitude persists because space cells must deliver 28-34% efficiency under extreme radiation and thermal stress"
"Metal halide perovskites present a promising option." for a future technology
Fabrication process much simpler than crystal growth required for III-V cells.
Market Report Analytics
The unit cost per watt for these cells is significantly higher than traditional silicon solar cells, often ranging from $50-150 per watt or more"
Redwire Space Roll Out Solar Array (ROSA)
ROSA is used on the ISS
Several configurations are listed on the datasheet
The average derived W/kg is 96 W/kg
Source Energy Gen 3 Mini Solar Module
Specific Powers up to 303 W/kg
Full electrical redundancy
Tolerant to micrometeroites and localized shading
Space grade materials
15.6W module
$462 at 15,000 volume
| 29.6154 | $/W at scale
Unclear if this is a typical III-V gallium arsenide solar cell or if this is a new technology
Flight heritage on SpaceX Transport 8 and 9 but production likely not in the constellation scale yet ($/W unproven)
Starlight Air
Cites industry standard today at $100/W
New thin film design in Starlight Air
3000 W/kg
$15/W
Targeting 50 MW/year production
Key Takeaways
As multiple sources pointed out, the industry standard (III-V gallium arsenide) stands at ~$100/W, but these likely aren't at the extreme scale that an ODC might be at
We can apply a generous 50% reduction of the current standard for an estimate of the GW-scale price-volume discounts
Source Energy represents a promising new standard at $29.62/W and 303 W/kg. This represents a safe next gen state at ODC scale.
Starlight Air is the kind of radical technology change that is needed here, but it is only a lab prototype. $15/W and 3000 W/kg for future limits.
Metric: Radiator Operating Temp (K)
NVIDIA H100 PCIe GPU
"Thermal qualification temperature = 87 degrees C"
This is max operating temperature but not recommended for sustained operations.
Real data center deployment typically hold GPU junction temperatures in the 75-83C range
Assume 350K for 24/7 workload
Franhofer IMS / IMAPS HiTEC Conference (2012)
"Standard bulk CMOS technology targets operating temperature of not more than 175C. Silicon-on-insulator technologies are commonly used up to 250C"
The fundamental physics limit for bulk silicon CMOS is around 175 C (448K) before reliability mechanisms degrade unacceptably.
SOI processes extend this to 250C but at the cost of performance density.
Automotive-grade Ics are already qualified to AEC-Q100 Grade 0 at Tj_max=150C
Synopsys / TSMC AEC-Q100 Grade 1 Qualification (2016)
"DesignWare Foundation IP meets automotive Grade 1 temperature (-40C to +150C junction) requirements"
TSMC's 16nm FinFET process (same general family as data center nodes) has been qualified up to 150C (423K) for automotive applications
--> Assume 400 K (127C) as the Next Gen 5-year mark - achievable with purpose-built silicon using existing known processes
Possible consequences include shorter lifetimes and/or worse reliability
NASA Glenn Research Center - Silicon Carbide Electronics and Sensors Link
"SiC devices have repeatedly remonstrated operation above 500 C, far exceeding the temperature limits of Si-based electronics"
NASA Science - Integrated Circuits to Enable Exploration of the Harshest Environments Link
"Newly developed silicon carbide electronics have operated in ovens for over a year at 500C and for 60 days in simulated Venus conditions"
These are 195-transistor simple logic circuits, comparable in complexity to 1970s-era electronics.
These technologies are likely too much in their infancy to assume ready for space GPU production in the next 10 years.
--> Recommend taking 500 K (227 C) as the Future Limits 10-year mark
This sits at the upper end of what SOI silicon CMOS can deliver and a possible "de-rated" case for a SiC technology
Metric: Effective Emissivity ε
AZ-93
"emitting 89-93% of the internal heat generated"
Gold standard today
Vantablack
"The apparent temperature of a blackbody coated with Vantablack-S (MWIR emissivity >99.7%), would be 20.009C"
Imaging and Machine Vision Europe
"In the MWIR, emissivity is greater than 99.8%; in the LWIR, it is greater than 99.5%"
--> Carbon nanotube-based coatings like Vantablack S-IR achieve emissivities of 0.995-0.998 in laboratory today.
Vantablack coating has been through partial space qualification including shock, vibration, thermal cycling, and outgassing.
Unproven at scale
Only works if radiator is thermally shielded from sun (must be in SSO facing away)
Approach: use 0.95 as next gen 5-year mark, 0.97 as future limits 10-year mark
Metric: Radiator Mass Density (kg/m^2)
MetalLock Honeycom Systems
Total thickness: 20 mm
Weight: 6.3 kg/m^2
Space Mission Analysis and Design (textbook)
Table 11-45. Thermal Hardware Mass and Power Estimates
Radiator panels: 3.3 kg/m^2
Passive panel without deployment mechanism
Redwire Space Q-Rad Deployable Radiator
"Areal density 3.5 to 4.9 kg/m^2"
“Leveraging ultra-high thermal conductivity solid-state materials, Q-Rad is a compact, lightweight, modular, and passive thermal control solution”
This is the subsystem-level areal density (panel + high-strain ccomposite hinges + heat transport)
Because it's deployable, it radiates on both sides
Small and thin - may not scale to adequate satellite size
The Aerospace Corporation
Chart showing some state-of-the-art passive deployable radiators fall in line with the 6 kg/m^2 goal
Table also shows max operating temperatures of 100-120 C, potentially constraining max W output
--> Passive deployable radiators are the best combination of simplicity (better than active) and heat rejection (better than single-sided)
These radiators are sheets or honeycomb structures of conductive material, deployed with simple mechanisms
The kg/m^2 will be higher (due to mechanisms) than a fixed structure, but the radiation efficacy will be double
We'll take 6 kg/m^2 as a moderate ambition today, with potential optimized versions dropping down to 5 or 4 kg/m^2 in the future.
Metric: Radiator Cost Density ($/m^2)
Space-grade deployable passive radiator costs are not readily available online. We must build up an estimate from component material costs.
Component 1: Aluminum Face Sheets (2x0.020" 5052)
Mass: 2*0.000508m*2680 kg/m^3=2.72 kg/m^2 (first principles + aluminum density)
Aircraft Spruce
Retail cost: $115.99 for a 0.032" thick sheet
48x72"=2.23m^2. That's $52/m^2
Scaling linearly to 0.020" --> $33/m^2 per sheet
Two sheets = ~$66/m^2 at retail
Machine Mfg indicates approximately $1.526/lb
Metal value approximately $1.526/lb as of June 2025
$3.36/kg
Contained metal value, not finished thin-gauge sheet.
Finished sheet would carry a rolling/slitting premium; 1.5-2x metal value
~$5-7/kg
Two face sheets at 2.72 kg/m^2 * $5-7/kg = ~$14-19/m^2 at bulk
Component 2: Honeycomb Core
ACP Composites
$99.42 through $593.24 for large-format HexWeb sheets
48x96" sheet = 2.97 m^2.
Mid-range estimate at $100/m^2 at retail
Bulk pricing may (aggressively) be 50% of retail: $50/m^2
Component 3: AZ-93
This is likely a very thin coating, and the exact $/m^2 will likely fall into the noise of the other assumptions.
Component 4: Deployment Mechanism
Since deployable radiators effectively double the radiator area, the cost factor should be less than 2x
Rough approximation is 1.5x material cost.
Current subtotal is ~$70/m^2, making a deployable version $105/m^2
Component 5: Manfuacturing & Space Qualification Multiplier
Rough approximation given the state of aerospace manufacturing industry, but perhaps a 2x factor on direct material cost.
This puts material/manufacturing cost at $210/m^2 today.
With optimized/automated manufacturing, this cost could be reduced another 10% in subsequent generations.
Metric: Integration Systems Mass Factor
Space Mission Analysis and Design (textbook)
Table A-2 Mass Distribution for Selected Spacecraft
|  | Structure | 21.7% |  | an integrated solar/compute/radiator sandwich could reduce this structural cost greatly
|  | TT&C | 7.5% | "Avionics"
|  | ADCS | 8% | "Avionics"
|  | Propulsion | 3.7%
Disclaimer: none of the satellites listed are for "compute" missions; ODCs may represent fundamentally different distributions here.
These are common "integration" factors that don't change much over time with new technology; perhaps a radically different architecture could change these.
There is no need to distinguish these components at this stage, so we will call this "integration systems" at 40.9% mass factor
Metric: Integration Systems Cost Factor
Integration subsystems (structure, propulsion, avionics) represent approximately 25-35% of total satellite bus manufacturing cost.
This is the most weakly support estimate based on public information. We draw this from a few parallels:
SMAD mass fractions:
Structure + ADCS + TT&C + Propulsion = ~42% of conventional satellite dry mass
Cost fraction is slightly lower than mass fraction because structure (the largest component) is the cheapest per kg, while avionics (the smallest) is the most expensive
Applying a modest discount for cost-vs-mass yields 30-35%
Automotive analogy
In automotive manufacturing, the structural, wiring, and electronic integration functions represent ~25-35% of vehicle manufacturing cost - a well-document ratio across the industry
The analogy holds because both domains involve a structural frame supporting functional subsystems with power distribution and control electronics
Apex bus pricing as a bound:
Apex sells complete buses (structure + power + propulsion + avionics + thermal, excluding payload) for #3.5-9.5M at low volume
For a typical mission, the bus represents 15-50% total satellite cost
Within the bus itself, power and thermal are distinct subsystems that this model already prices separately
The remaining integration fraction (structure + propulsion + avionics) is roughly 25-35% of the total
Launch Vehicle Metrics
SpaceX Falcon 9
Payload to LEO, resuable: 17,500 kg
Price per Launch: ~$70M
Price per kg: $4000/kg
Estimated internal cost per launch: $28M
Estimated internal cost per kg: $1600/kg
Launch rate: 167 launches/year demonstrated in 2025
"This year and next year I anticipate will be the highest Falcon launch rates that we will see"
Next Gen : Starship V3 early operations with some reuse
SpaceX Payload Users Guide
"At the baseline reusable design, Starship can deliver over 100 metric tons to LEO"
NASASpaceflight, May 2025 (https://www.nasaspaceflight.com/2025/05/future-starship-block-3-mars/)
"will increase the Ship's payload capacity by 40 tons, bringing it to approximately 100+ tons reusable"
Block 3 with Raptor 3 engines; 100T is the conservative operational floor
Wikipedia (https://en.wikipedia.org/wiki/SpaceX_Starship)
Block 2 "was planned to have a payload capacity of at least 100 tons to orbit when reused" but retired at 35T actual; Block 3 restores this target
SpaceNews, March 2026 (https://spacenews.com/starlab-space-fully-books-commercial-payload-space-on-planned-space-station/)
"In the company's 10-K filing, it said it has a launch contract priced at $90 million to send Starlab to orbit"
Only publicly disclosed, legally binding Starship commercial price as of early 2026
Basenor, March 2026 (https://www.basenor.com/blogs/news/spacex-scores-90m-starship-contract-to-launch-starlab-space-station)
"now we know the actual contracted number landed at $90 million"
At 100T payload @ $90M → $900/kg
Elon Musk tweeted early 2025 targeting ~1 Starship launch/week within a year; actual 2025 result was 5 flights
SpaceX Falcon 9 precedent: 18 launches in 2017 → 61 by 2022 (5 years). Comparable early ramp supports 52/yr within ~5 years of first operational Starship flights
Wikipedia (https://en.wikipedia.org/wiki/List_of_Starship_launches)
"Starship was launched just five times in 2025"
Confirms current state vs. aspiration gap; 52/yr is a conservatively adjusted Elon timeline
Future Concept : Mature Starship with heavy reuse
Elon Musk, September 2024 (https://starship-spacex.fandom.com/wiki/Ship_(Starship%27s_Second_Stage))
"Max payload to standard Earth reference orbit is actually ~180 tons for Starship when it is fully reusable and ~300 tons if expendable"
New Space Economy, Dec 2025 (https://newspaceeconomy.ca/2025/12/12/the-heavy-lifters-a-comparative-analysis-of-launch-vehicle-payload-capacities/)
"The future V3 variant, featuring stretched tanks and improved engines, is projected to double this capacity to at least 200 metric tons reusable, or potentially 400 tons expendable"
NASASpaceflight, May 2025 (https://www.nasaspaceflight.com/2025/05/future-starship-block-3-mars/)
Further stretch to 142m total length planned; 200T is a reasonable mature-state estimate for ~10yr horizon
The 10-year performance is aspirational; we'll use 200T as the target
NextBigFuture, Jan 2025 (https://www.nextbigfuture.com/2025/01/spacex-starship-roadmap-to-100-times-lower-cost-launch.html)
At $90M build cost: "For 20 Flights: With 200 tons payload: $32.50 per kg" … "For 50 Flights: With 200 tons payload: $19.00 per kg"
NextBigFuture, Aug 2025 (https://www.nextbigfuture.com/2025/08/spacex-launch-will-be-five-times-lower-cost-for-end-of-2025.html)
"Estimated operational cost with high reuse rate (e.g., 100+ flights per booster): $10-15 million per launch, or ~$67-100 per kg for 150-ton payloads"
Derived: $100/kg × 200,000 kg = $20M/launch. $100/kg is well above SpaceX's aspirational $10-20/kg internal cost but gives ODC generous benefit of the doubt; within range of credible independent estimates
SpaceNews, Jan 2026 (https://spacenews.com/spacex-plans-next-starship-test-flight-in-march/)
"SpaceX received approval in November to convert Space Launch Complex 37 at Cape Canaveral Space Force Station… into a Starship complex with two launch pads"
5+ pads across 3 sites (Starbase 2 pads, KSC LC-39A, CCSFS SLC-37 2 pads); 1 launch/day physically achievable at ~10yr maturity with rapid reuse architecture
ODC Operations
Analog 1: Iridium NEXT - 66 satellites, $178M/year ops
Cost of services (excl. D&A): $178.1M full-year 2024 (Iridium Q4 2024 8-K)
Scope includes "network engineering and operations staff, including contractors, software maintenance, product support services" (Iridium 2023 ARS)
Total constellation CapEx: ~$3B for 75 satellites launched, 66 operational + 9 spares (Iridium press release, Feb 2019)
That's ~6% of CapEx/year, but a large portion is customer-facing telecom ops (billing, provisioning, partner management, hosted payloads) that an ODC wouldn't have
Pure constellation management (flight dynamics, TT&C, anomaly resolution, software) is probably 40-50% of the total, or ~$70-90M/year
Analog 2: Starlink - ~10,000 satellites, ~$1.5B/year ops (estimated)
One estimate: "$1.5 Billion per year operation cost (ground and salary)" (NextBigFuture, May 2022)
"SpaceX has more than 13,000 employees, of which roughly 3,000 work for Starlink" (Quilty Space, July 2025)
At ~$200K fully-loaded per head, that's ~$600M/year in headcount alone
Starlink ops include massive customer operations: 10M subscribers, billing in 150 countries, terminal logistics, spectrum coordination, customer support
Pure constellation management (mission control, collision avoidance, software updates for 10,000+ sats) is likely $300-500M/year
What ODC ops scope may looks like
No end-user customers : the "customer" is the operator's own AI workload
No billing, consumer support, terminal logistics, or spectrum coordination for user links
Scope: mission control, flight dynamics, collision avoidance, attitude control, TT&C monitoring, anomaly resolution, software/firmware updates, ground station leases, cybersecurity, regulatory compliance (ITU, debris mitigation)
More comparable to a military/scientific constellation than a commercial telecom constellation
Scaling Logic
Traditional single-satellite ops: ~$1M/year per satellite (Armada International, 2020)
Iridium: $178M / 66 sats = $2.7M/sat — but includes all customer-facing business
Starlink pure constellation ops: ~$300-500M / 10,000 sats = $30-50K/sat — automation makes marginal satellite nearly free
ODC range: 43 satellites (Future Concept) to 1,879 satellites (Tech Today)
At $50K/sat, Tech Today = $94M/year; at the low end, fixed costs dominate
$250M/year flat is ~1.4× Iridium's total cost of services, consistent with estimated Starlink constellation-management costs scaled down, and represents a steady-state team of 500-1,000 aerospace engineers/operators : conservative but not nonsensical